## Revision
IVRF_Protocol_Document
Current Revision No
12
Revision No | Date | Changes in Brief | Done By | Colour Code
1 | 2014-01-17 | user and Engg frame change from DVRF to IVRF | Sagar C
2 | 2014-02-04 | In Config upload and download reply frame, IVRF identifier added | Sagar C
3 | 2015-02-05 | 1.New IDU capacities added in "User frame", "IDU Parameter", "Configuration Upload", "Configuration Download" sheets. 2.IDU Backup mode command added in "ODU-IDU Normal Comm" sheet. 3.Filter Reset command added in"IDU Parameters Upload" Sheet. | Suraj C
4 | 2017-09-26 | 1. Added Capcity codes for different capacities of SIAM compressor | Prathamesh S
5 | 2023-09-26 | Communication Sequence details added. For 6th Gen VRF - Fan Drive parameters & New sensor added in Engineering frame. | Danish Ahmed
6 | 2023-10-05 | Compressor Drive Firmware verision added in Engineering Frame in future use bytes. ODUm-ODUs Communication protocol updated for all above parameter. | Danish Ahmed
7 | 2024-03-04 | 1. Fan Drive 2 parameters added in ODUm-ODUs Communication protocol 2. Byte values added based on VRF V Plus firmware in ODUm-ODUs Communication protocol. 3. Oil Level Byte value added in Engineering Frame. | Danish Ahmed
8 | 2024-05-24 | 1. Oil Level values defination changed in Engineering Frame & ODUm-ODUs frame. 2. Comp. Drive FW version format changed to Hex instead of ASCII in Engineering Frame & ODUm-ODUs frame. | Danish Ahmed
9 | 2024-06-05 | 1. Oil Level values defination changed in Engineering Frame & ODUm-ODUs frame. | Danish Ahmed
10 | 2024-10-10 | 1. Reverse Rotation command added between Master & Slave. 2. Slave Ambient Protection State added between Master & Slave in Reserved Byte. | Danish Ahmed
11 | 09--Jan-25 | 1. In IVRF Engineering frame,For 6th gen, Oil temp 1, Oil temp 2, Suction temp, Fan Drive 1 current, Fan Drive 2 current after decimal conversion value to be divided by 10 2. In IVRF Engineering frame, For 5th & 6th gen, Liq Inj, parameter description of 0,1 and 2 level added 3. In IVRF Engineering frame, For 6th gen, Protections CP1, CP2, IT1, IT2 added | Sneha Shirsat
12 | 16--Feb--2026 | Added IDU Model type of 1-way CST identification | Amey Samant

## Communication Sequence
VRF IV Plus, V Plus & VRF VI Plus Communication Protocol Frames Explanation: | [5 empty] | SF | Special Feature (Debugger)
Date -31-8-2023 | [5 empty] | ODUm | Master ODU Controller
[6 empty] | ODUs | Slave ODU Controller
[6 empty] | IDU | IDU Controller
| Sr No | Frame Name | Purpose | Communication Line | Master | Slave | Interval | Commn settings
| 1 | IVRF Engineering Frame | Command Frame From PC Monitoring to ODU Master of System for Engineering Data Reply Send from ODU Master of System to PC Monitoring for User data | A2B2 SF-ODUm | SF | ODUm | Event Based As fast as every 1 second Request can come | Baud Rate : 57600 Parity : None Stop Bit : 1 Data Bits : 8
| 2 | IVRF User Frame | Command Frame From PC Monitoring to ODU Master of System for User Data Reply Send from ODU Master of System to PC Monitoring for User Data | A2B2 SF-ODUm | SF | ODUm | Event Based | Baud Rate : 57600 Parity : None Stop Bit : 1 Data Bits : 8
| 3 | IVRF ODU Parameters | Frame From PC Monitoring to ODU Masters for ODU Parameters | A2B2 SF-ODUm | SF | ODUm | Event Based | Baud Rate : 57600 Parity : None Stop Bit : 1 Data Bits : 8
| 4 | IDU Parameters | Frame From PC Monitoring to ODU Master for IDU Parameters | A2B2 SF-ODUm | SF | ODUm | Event Based | Baud Rate : 57600 Parity : None Stop Bit : 1 Data Bits : 8
| 5 | IVRF Configuration Download | Frame From PC Monitoring to ODU Master for Configuration Download Request Reply From ODU Master to PC Monitoring for Configuration Download | A2B2 SF-ODUm | SF | ODUm | Event Based | Baud Rate : 57600 Parity : None Stop Bit : 1 Data Bits : 8
| 6 | IVRF Configuration Upload | From PC Monitoring to ODU Master for Configuration Upload ACK or NACK Frame From ODU Master to PC Monitoring | A2B2 SF-ODUm | SF | ODUm | Event Based | Baud Rate : 57600 Parity : None Stop Bit : 1 Data Bits : 8
| 7 | ODUm-ODUs Communication | Frame From ODU Master to Slave for Data Reply From Slave to ODU Master for Slave Data | A1B1 ODUm-ODUs | ODUm | ODUs x 3 | Every 10 seconds | Baud Rate : 9600 Parity : None Stop Bit : 1 Data Bits : 8
| 8 | ODU-IDU Communication | Frame From ODU Master to IDU for IDU Data Reply From IDU to ODU Master for Data | A1B1 ODUm-IDU | ODUm | IDUs x 64 | Every 10 seconds After slave commn is completed | Baud Rate : 9600 Parity : None Stop Bit : 1 Data Bits : 8
| 9 | IVRF Slave ODU Parameters | Frame From ODU Master to Slave for Slave Parameter upload | A1B1 ODUm-ODUs | ODUm | ODUs x 3 | Event Based | Baud Rate : 9600 Parity : None Stop Bit : 1 Data Bits : 8
| 10 | Slave Config Download | Frame From ODU Master to Slave for Slave Configuration Download Request Reply From Slave to ODU Master for Slave Configuration Download | A1B1 ODUm-ODUs | ODUm | ODUs x 3 | Event Based | Baud Rate : 9600 Parity : None Stop Bit : 1 Data Bits : 8
| 11 | Slave Config Upload | Frame From ODU Master to Slave for Slave Configuration Upload Reply From Slave to ODU Master for Slave Configuration Upload | A1B1 ODUm-ODUs | ODUm | ODUs x 3 | Event Based | Baud Rate : 9600 Parity : None Stop Bit : 1 Data Bits : 8
| 12 | Set IDU Parameters | Frame From ODU Master to IDU for IDU Parameters Upload | A1B1 ODUm-IDU | ODUm | IDUs x 64 | Event Based | Baud Rate : 9600 Parity : None Stop Bit : 1 Data Bits : 8
| 13 | IDU Config Download | Frame From ODU Master to IDU for Configuration Download Request Reply From IDU to ODU Master for Configuration Download | A1B1 ODUm-IDU | ODUm | IDUs x 64 | Event Based | Baud Rate : 9600 Parity : None Stop Bit : 1 Data Bits : 8
| 14 | IDU Config Upload | Frame From ODU Master to IDU for Configuration Upload Reply From IDU to ODU Master for Configuration Upload | A1B1 ODUm-IDU | ODUm | IDUs x 64 | Event Based | Baud Rate : 9600 Parity : None Stop Bit : 1 Data Bits : 8
| 15 | Auto Addressing | Frame From ODU Master to IDU for Start of Autoadressing Frame From ODU Master to IDU for Who is IDU 'X' Reply Frame From IDU to ODU Master for Who is IDU 'X' Frame From ODU Master to IDU for Recalculation Frame From ODU Master to IDU for IDU ID Confirmation Reply Frame From IDU to ODU Master for IDU ID Confirmation Frame From ODU Master to IDU for End of Autoadressing | A1B1 ODUm-IDU | ODUm | IDUs x 64 | Event Based | Baud Rate : 9600 Parity : None Stop Bit : 1 Data Bits : 8
| 16 | Start of BL Session | Frame From PC Monitoring to ODU Master for Start of Bootloader Session Command Frame From ODU Master to Slave or IDU for Start of Bootloader Session Command ACK or NACK Frame From ODU Master to PC Monitoring | x | x | x | x | x
| 17 | Block Programming | Frame From PC Monitoring to ODU Master for Block Programming Frame From ODU Master to Slave or IDU for Block Programming ACK or NACK Frame From ODU Master to PC Monitoring | x | x | x | x | x
| 18 | BL Status Polling | Frame From PC Monitoring to ODU Master for Status Polling Reply Frame From ODU Master to PC Monitoring for Programming Status of master Reply Frame From ODU Master to PC Monitoring for Programming Status of IDUs and Slave Frame From ODU Master to Slave or IDU for Status Polling Reply Frame From Slave or IDU to ODU Master for Programming Status | x | x | x | x | x
| 19 | End of BL Session | Frame From PC Monitoring to ODU Master for End of Bootloader Session Command Frame From ODU Master to Slave or IDU for Start of Bootloader Session Command ACK or NACK Frame From ODU Master to PC Monitoring | x | x | x | x | x
| 20 | DC, Moddbus, DA Config | Frame From PC Application to Data Concentrator or Data Acq module or Modbus Converter for no of systems connected Frame From Data Concentrator or Data Acq module or Modbus Converter to PC Application for acknowledgment | x | x | x | x | x
| 21 | Date Time Config in DA | Request Frame From PC Application to Data Acq module for Date and time Frame From PC Application to Data Acq module or vice versa for Date and time Frame From Data Acq module to PC Application for acknowledgment | x | x | x | x | x
| 22 | Data Acq Communication | Request Frame From PC Application to Data Acq module for Data Reply Frame From Data Acq module to PC for Data Reply Frame From Data Acq module to PC for Data | x | x | x | x | x
| 23 | IVRF Error Logging | ODU Error Log Request by PCM ODU Error Log Upload by ODU Master IDU Error Log Upload by ODU Master | A2B2 SF-ODUm | SF | ODUm | Event Based
| 24 | ODU Config | Command Frame From Debugger to ODU for ODU Configuration and Auto Address Reply Send from ODU Master | A2B2 SF-ODUm | SF | ODUm | Event Based

## IVRF Engineering Frame
[6 empty] | Issues or changes | ODU Firmware change required?
Command Frame From PC Monitoring to ODU Master of System for Engineering Data
* ¦ P¦ C ¦ Frame Count ¦ Syatem ID ¦ Command¦ Data Type(E) ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description | Parameter | Description
0 | 1 | * | Start of frame | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master | P | Frame from PC Monitoring to ODU Master
2 | 1 | C | Command Frame | C | Command Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C | No. of characters in the Frame before CRC including '*' =in Hex= | FFFFFFFFFB
5 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
7 | 2 | Command | For System Status Data 01d=(01)h=(0x30,0x31)ASCII | Command | For System Status Data 01d=(01)h=(0x30,0x31)ASCII
9 | 1 | Data Type | For Engineering data 'E' = 0x45 | Data Type | For Engineering data 'E' = 0x45
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data | # | End of Data
17
Reply Send from ODU Master of System to PC Monitoring for User data
* ¦ M¦ D ¦ XXI ¦ System Data ¦ Syatem ID¦ Data Type(E) ¦ Protocol Version no ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description | Parameter | Description
0 | 1 | * | Start of frame | * | Start of frame
1 | 1 | M | Frame From Master to PC monitoring | M | Frame From Master to PC monitoring
2 | 1 | D | Data Frame | D | Data Frame
3 | 3 | XXI | IVRF | XXI | IVRF
6 |  | System Info |  | System Info
6 | 1 | System 3min OFF | 0x30 = OFF 0x31 = ON Bool | System 3min OFF | 0x30 = OFF 0x31 = ON Bool
7 | 2 | IDUqty | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned Char | IDUqty | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned Char
9 | 3 | ΣODU | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII Unsigned int | ΣODU | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII Unsigned int
12 | 4 | ΣIDU | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCIIt Unsigned int | ΣIDU | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCIIt Unsigned int
16 | 3 | Diversity | Range:(0-150)d=(provision for 0-999)d= (0x30,0x30,0x30-0x33,0x45,0x37)ASCII Unsigned int | Diversity | Range:(0-150)d=(provision for 0-999)d= (0x30,0x30,0x30-0x33,0x45,0x37)ASCII Unsigned int
19 | 4 | ΣThermoON | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int | ΣThermoON | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
23 | 4 | TMC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int | TMC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
27 | 4 | TSCnew | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int | TSCnew | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
31 | 4 | TSCold | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int | TSCold | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
35 | 4 | BTCnew | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII Unsigned int | BTCnew | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII Unsigned int
39 | 4 | BTCold | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII Unsigned int | BTCold | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII Unsigned int
43 | 1 | ODU Mode | 0x30 = Off 0x31 = Heat 0x32 = Cool 0x33 = Free Unsigned char | ODU Mode | 0x30 = Off 0x31 = Heat 0x32 = Cool 0x33 = Free Unsigned char | 0x30 = Free 0x31 = Heat 0x32 = Cool 0x33 = Off Unsigned char | No
44 | 1 | ODU Mode Act | 0x30 = Off 0x31 = Heat 0x32 = Cool Unsigned char | ODU Mode Act | 0x30 = Off 0x31 = Heat 0x32 = Cool Unsigned char
45 | 10 | ODU RTC | DD:MM:YY, HH:MM | ODU RTC | DD:MM:YY, HH:MM
55 |  | Switch |  | Switch
55 | 1 | PERF | 0x30 = OFF 0x31 = ON Bool | PERF | 0x30 = OFF 0x31 = ON Bool | Not implemented in ODU F/W | Yes
56 | 1 | CHKM | (0-15)d = (0-F)h Unsigned Char | CHKM | (0-15)d = (0-F)h Unsigned Char
57 | 1 | SLTM |  | SLTM
58 | 1 | SLTL |  | SLTL
59 | 1 | DMDM |  | DMDM
60 | 1 | DMDL |  | DMDL
61 |  | General Info Master |  | General Info Master
61 | 1 | CAP | VRF ODU Capacity Codes 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP 0x46 = 'F' = 4 HP 0x47 = 'G' = 5 HP 0x48 = 'H' = 6 HP | CAP | VRF ODU Capacity Codes 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP 0x46 = 'F' = 4 HP 0x47 = 'G' = 5 HP 0x48 = 'H' = 6 HP
62 | 4 | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
66 | 1 | Defrost | 0x30 = Normal 0x31 = Go defrost Unsigned Char | Defrost | 0x30 = Normal 0x31 = Go defrost Unsigned Char
67 | 1 | Self oil recovery | 0x30 = Normal 0x31 = Do Self oil recovery 0x32 = 0x33 = Unsigned Char | Self oil recovery | 0x30 = Normal 0x31 = Do Self oil recovery 0x32 = 0x33 = Unsigned Char
68 | 1 | Oil Swap | 0x30 = Normal 0x31 = 0x32 = Supplier 0x33 = Receiver Unsigned Char | Oil Swap | 0x30 = Normal 0x31 = 0x32 = Supplier 0x33 = Receiver Unsigned Char
69 | 1 | Liquid inject | 0x30 = 0 0x31 = 1 0x30 = 2 Unsigned Char | Liquid inject | 0x30 = 0 0x31 = 1 0x30 = 2 Unsigned Char
70 | 3 | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned int | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned int
73 | 1 | ODU 3 min OFF | 0x30 = OFF 0x31 = ON Bool | ODU 3 min OFF | 0x30 = OFF 0x31 = ON Bool
74 | 1 | Inv1 3 min off |  | Inv1 3 min off
75 | 1 | Inv2 3 min off |  | Inv2 3 min off
76 | 4 | Nominal Capacity |  | Nominal Capacity
80 | 4 | Max Capacity |  | Max Capacity
84 | 3 | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII Unsigned int | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII Unsigned int
87 | 2 | Master F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char | Master F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
89 | 2 | SPPR F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char | Fan Drive 1 FW version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
91 | 2 | Fan F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char | Fan Drive 2 FW version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
93 |  | General Info Slave 1 |  | General Info Slave 1
93 | 1 | CAP | VRF ODU Capacity Codes 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP 0x46 = 'F' = 4 HP 0x47 = 'G' = 5 HP 0x48 = 'H' = 6 HP | CAP | VRF ODU Capacity Codes 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP 0x46 = 'F' = 4 HP 0x47 = 'G' = 5 HP 0x48 = 'H' = 6 HP
94 | 4 | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
98 | 1 | Defrost | 0x30 = Normal 0x31 = Go defrost Unsigned Char | Defrost | 0x30 = Normal 0x31 = Go defrost Unsigned Char
99 | 1 | Self oil recovery | 0x30 = Normal 0x31 = Do Self oil recovery 0x32 = 0x33 = Unsigned Char | Self oil recovery | 0x30 = Normal 0x31 = Do Self oil recovery 0x32 = 0x33 = Unsigned Char
100 | 1 | Oil Swap | 0x30 = Normal 0x31 = 0x32 = Supplier 0x33 = Receiver | Oil Swap | 0x30 = Normal 0x31 = 0x32 = Supplier 0x33 = Receiver
101 | 1 | Liquid inject | 0x30 = 0 0x31 = 1 0x30 = 2 Unsigned Char | Liquid inject | 0x30 = 0 0x31 = 1 0x30 = 2 Unsigned Char
102 | 3 | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned int | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned int
105 | 1 | ODU 3 min OFF | 0x30 = OFF 0x31 = ON Bool | ODU 3 min OFF | 0x30 = OFF 0x31 = ON Bool
106 | 1 | Inv1 3 min off |  | Inv1 3 min off
107 | 1 | Inv2 3 min off |  | Inv2 3 min off
108 | 4 | Nominal Capacity |  | Nominal Capacity
112 | 4 | Max Capacity |  | Max Capacity
116 | 3 | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII Unsigned int | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII Unsigned int
119 | 2 | Master F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCIIt Unsigned i | Master F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCIIt Unsigned i
121 | 2 | SPPR F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned int | Fan Drive 1 FW version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
123 | 2 | Fan F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned int | Fan Drive 2 FW version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
125 |  | General Info Slave 2 |  | General Info Slave 2
125 | 1 | CAP | VRF ODU Capacity Codes 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP 0x46 = 'F' = 4 HP 0x47 = 'G' = 5 HP 0x48 = 'H' = 6 HP | CAP | VRF ODU Capacity Codes 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP 0x46 = 'F' = 4 HP 0x47 = 'G' = 5 HP 0x48 = 'H' = 6 HP
126 | 4 | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
130 | 1 | Defrost | 0x30 = Normal 0x31 = Go defrost Unsigned Char | Defrost | 0x30 = Normal 0x31 = Go defrost Unsigned Char
131 | 1 | Self oil recovery | 0x30 = Normal 0x31 = Do Self oil recovery 0x32 = 0x33 = Unsigned Char | Self oil recovery | 0x30 = Normal 0x31 = Do Self oil recovery 0x32 = 0x33 = Unsigned Char
132 | 1 | Oil Swap | 0x30 = Normal 0x31 = 0x32 = Supplier 0x33 = Receiver | Oil Swap | 0x30 = Normal 0x31 = 0x32 = Supplier 0x33 = Receiver
133 | 1 | Liquid inject | 0x30 = 0 0x31 = 1 0x30 = 2 Unsigned Char | Liquid inject | 0x30 = 0 0x31 = 1 0x30 = 2 Unsigned Char
134 | 3 | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned int | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned int
137 | 1 | ODU 3 min OFF | 0x30 = OFF 0x31 = ON Bool | ODU 3 min OFF | 0x30 = OFF 0x31 = ON Bool
138 | 1 | Inv1 3 min off |  | Inv1 3 min off
139 | 1 | Inv2 3 min off |  | Inv2 3 min off
140 | 4 | Nominal Capacity |  | Nominal Capacity
144 | 4 | Max Capacity |  | Max Capacity
148 | 3 | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII Unsigned int | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII Unsigned int
151 | 2 | Master F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCIIt Unsigned i | Master F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCIIt Unsigned i
153 | 2 | SPPR F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned int | Fan Drive 1 FW version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
155 | 2 | Fan F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned int | Fan Drive 2 FW version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
157 |  | General Info Slave 3 |  | General Info Slave 3
157 | 1 | CAP | VRF ODU Capacity Codes 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP 0x46 = 'F' = 4 HP 0x47 = 'G' = 5 HP 0x48 = 'H' = 6 HP | CAP | VRF ODU Capacity Codes 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP 0x46 = 'F' = 4 HP 0x47 = 'G' = 5 HP 0x48 = 'H' = 6 HP
158 | 4 | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
162 | 1 | Defrost | 0x30 = Normal 0x31 = Go defrost Unsigned Char | Defrost | 0x30 = Normal 0x31 = Go defrost Unsigned Char
163 | 1 | Self oil recovery | 0x30 = Normal 0x31 = Do Self oil recovery 0x32 = 0x33 = Unsigned Char | Self oil recovery | 0x30 = Normal 0x31 = Do Self oil recovery 0x32 = 0x33 = Unsigned Char
164 | 1 | Oil Swap | 0x30 = Normal 0x31 = 0x32 = Supplier 0x33 = Receiver | Oil Swap | 0x30 = Normal 0x31 = 0x32 = Supplier 0x33 = Receiver
165 | 1 | Liquid inject | 0x30 = 0 0x31 = 1 0x30 = 2 Unsigned Char | Liquid inject | 0x30 = 0 0x31 = 1 0x30 = 2 Unsigned Char
166 | 3 | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned int | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned int
169 | 1 | ODU 3 min OFF | 0x30 = OFF 0x31 = ON Bool | ODU 3 min OFF | 0x30 = OFF 0x31 = ON Bool
170 | 1 | Inv1 3 min off |  | Inv1 3 min off
171 | 1 | Inv2 3 min off |  | Inv2 3 min off
172 | 4 | Nominal Capacity |  | Nominal Capacity
176 | 4 | Max Capacity |  | Max Capacity
180 | 3 | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII Unsigned int | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII Unsigned int
183 | 2 | Master F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCIIt Unsigned i | Master F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCIIt Unsigned i
185 | 2 | SPPR F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned int | Fan Drive 1 FW version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
187 | 2 | Fan F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned int | Fan Drive 2 FW version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
189 |  | Master Output |  | Master Output
189 | 3 | Set RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | Set RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
192 | 3 | Set RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | Set RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
195 | 3 | F/b RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | F/b RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
198 | 3 | F/b RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | F/b RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
201 | 1 | 4W V | 0x30 = OFF 0x31 = ON Bool | 4W V | 0x30 = OFF 0x31 = ON Bool
202 | 1 | SORV |  | SORV
203 | 1 | OPOV |  | OPOV
204 | 1 | ORCV |  | ORCV
205 | 1 | LIBA |  | LIBA
206 | 1 | LIA1 |  | LIA1
207 | 1 | MLQV |  | MLQV
208 | 1 | HOTD |  | HOTD
209 | 1 | ULV1 |  | ULV1
210 | 1 | ULV2 |  | ULV2
211 | 1 | AROLV |  | AROLV
212 | 3 | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII Unsigned int | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII Unsigned int | Range should be (0-3000)d=(0-BB8)h | No
215 | 3 | EXV2 Step |  | EXV2 Step
218 | 1 | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII Unsigned int | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII Unsigned int | Range should be (0-12)d=(0-C)h | No
219 | 3 | Fan1 RPM | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII Unsigned int | Fan1 RPM | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII Unsigned int
222 | 3 | Fan2 RPM |  | Fan2 RPM
225 |  | Slave 1 Output |  | Slave 1 Output
225 | 3 | Set RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | Set RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
228 | 3 | Set RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | Set RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
231 | 3 | F/b RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | F/b RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
234 | 3 | F/b RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | F/b RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
237 | 1 | 4W V | 0x30 = OFF 0x31 = ON Bool | 4W V | 0x30 = OFF 0x31 = ON Bool
238 | 1 | SORV |  | SORV
239 | 1 | OPOV |  | OPOV
240 | 1 | ORCV |  | ORCV
241 | 1 | LIBA |  | LIBA
242 | 1 | LIA1 |  | LIA1
243 | 1 | MLQV |  | MLQV
244 | 1 | HOTD |  | HOTD
245 | 1 | ULV1 |  | ULV1
246 | 1 | ULV2 |  | ULV2
247 | 1 | AROLV |  | AROLV
248 | 3 | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII Unsigned int | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII Unsigned int
251 | 3 | EXV2 Step |  | EXV2 Step
254 | 1 | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII Unsigned int | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII Unsigned int
255 | 3 | Fan1 RPM | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII Unsigned int | Fan1 RPM | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII Unsigned int
258 | 3 | Fan2 RPM |  | Fan2 RPM
261 |  | Slave 2 Output |  | Slave 2 Output
261 | 3 | Set RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | Set RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
264 | 3 | Set RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | Set RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
267 | 3 | F/b RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | F/b RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
270 | 3 | F/b RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | F/b RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
273 | 1 | 4W V | 0x30 = OFF 0x31 = ON Bool | 4W V | 0x30 = OFF 0x31 = ON Bool
274 | 1 | SORV |  | SORV
275 | 1 | OPOV |  | OPOV
276 | 1 | ORCV |  | ORCV
277 | 1 | LIBA |  | LIBA
278 | 1 | LIA1 |  | LIA1
279 | 1 | MLQV |  | MLQV
280 | 1 | HOTD |  | HOTD
281 | 1 | ULV1 |  | ULV1
282 | 1 | ULV2 |  | ULV2
283 | 1 | AROLV |  | AROLV
284 | 3 | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII Unsigned int | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII Unsigned int
287 | 3 | EXV2 Step |  | EXV2 Step
290 | 1 | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII Unsigned int | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII Unsigned int
291 | 3 | Fan1 RPM | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII Unsigned int | Fan1 RPM | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII Unsigned int
294 | 3 | Fan2 RPM |  | Fan2 RPM
297 |  | Slave 3 Output |  | Slave 3 Output
297 | 3 | Set RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | Set RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
300 | 3 | Set RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | Set RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
303 | 3 | F/b RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | F/b RPS1 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
306 | 3 | F/b RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int | F/b RPS2 | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
309 | 1 | 4W V | 0x30 = OFF 0x31 = ON Bool | 4W V | 0x30 = OFF 0x31 = ON Bool
310 | 1 | SORV |  | SORV
311 | 1 | OPOV |  | OPOV
312 | 1 | ORCV |  | ORCV
313 | 1 | LIBA |  | LIBA
314 | 1 | LIA1 |  | LIA1
315 | 1 | MLQV |  | MLQV
316 | 1 | HOTD |  | HOTD
317 | 1 | ULV1 |  | ULV1
318 | 1 | ULV2 |  | ULV2
319 | 1 | AROLV |  | AROLV
320 | 3 | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII Unsigned int | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII Unsigned int
323 | 3 | EXV2 Step |  | EXV2 Step
326 | 1 | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII Unsigned int | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII Unsigned int
327 | 3 | Fan1 RPM | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII Unsigned int | Fan1 RPM | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII Unsigned int
330 | 3 | Fan2 RPM |  | Fan2 RPM
333 |  | Priorities Master |  | Priorities Master
333 | 1 | Inv 1 | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII Unsigned Char | Inv 1 | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII Unsigned Char
334 | 1 | Inv 2 |  | Inv 2
335 | 1 | ODU Startup Flag |  | ODU Startup Flag
336 |  | Priorities Slave 1 |  | Priorities Slave 1
336 | 1 | Inv 1 | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII Unsigned Char | Inv 1 | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII Unsigned Char
337 | 1 | Inv 2 |  | Inv 2
338 | 1 | Startup |  | Startup
339 |  | Priorities Slave 2 |  | Priorities Slave 2
339 | 1 | Inv 1 | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII Unsigned Char | Inv 1 | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII Unsigned Char
340 | 1 | Inv 2 |  | Inv 2
341 | 1 | Startup |  | Startup
342 |  | Priorities Slave 3 |  | Priorities Slave 3
342 | 1 | Inv 1 | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII Unsigned Char | Inv 1 | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII Unsigned Char
343 | 1 | Inv 2 |  | Inv 2
344 | 1 | Startup |  | Startup
345 |  | Master Inputs |  | Master Inputs
345 | 3 | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
348 | 3 | Low pressure |  | Low pressure
351 | 3 | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII Unsigned int | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII Unsigned int | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | No
354 | 3 | Tsat corresponding to Low pressure |  | Tsat corresponding to Low pressure
357 | 3 | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
360 | 3 | DLT2 |  | DLT2
363 | 3 | Inv1 Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int | Inv1 Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
366 | 3 | Inv2 Current |  | Inv2 Current
369 | 3 | IPM T1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int | IPM T1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
372 | 3 | IPM T2 |  | IPM T2
375 | 3 | Inv1 DC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int | Inv1 DC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
378 | 3 | Inv2 DC |  | Inv2 DC
381 | 4 | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
385 | 4 | Tliq1 |  | Tliq1
389 | 4 | Tgas2 |  | Tgas2
393 | 4 | Tliq2 |  | Tliq2
397 | 4 | Tamb |  | Tamb
401 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned Char | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned Char
403 | 2 | Last err |  | Last err
405 | 1 | Vr | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII | Oil Temp1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
406 | 1
407 | 1
408 | 1 | Vy | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII Unsigned int | Oil Temp2 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
409 | 1
410 | 1
411 | 1 | Vb | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII Unsigned int | Suction Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
412 | 1
413 | 1
414 |  | Slave 1 Inputs |  | Slave 1 Inputs
414 | 3 | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
417 | 3 | Low pressure |  | Low pressure
420 | 3 | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII Unsigned int | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII Unsigned int
423 | 3 | Tsat corresponding to Low pressure |  | Tsat corresponding to Low pressure
426 | 3 | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int For Decimal, consider value to be /10 | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
429 | 3 | DLT2 |  | DLT2
432 | 3 | Inv1 Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int | Inv1 Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
435 | 3 | Inv2 Current |  | Inv2 Current
438 | 3 | IPM T1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int | IPM T1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
441 | 3 | IPM T2 |  | IPM T2
444 | 3 | Inv1 DC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int | Inv1 DC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
447 | 3 | Inv2 DC |  | Inv2 DC
450 | 4 | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
454 | 4 | Tliq1 |  | Tliq1
458 | 4 | Tgas2 |  | Tgas2
462 | 4 | Tliq2 |  | Tliq2
466 | 4 | Tamb |  | Tamb
470 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned Char | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned Char
472 | 2 | Last err |  | Last err
474 | 1 | Vr | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII | Oil Temp1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
475 | 1
476 | 1
477 | 1 | Vy | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII Unsigned int | Oil Temp2 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
478 | 1
479 | 1
480 | 1 | Vb | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII Unsigned int | Suction Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
481 | 1
482 | 1
483 |  | Slave 2 Inputs |  | Slave 2 Inputs
483 | 3 | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
486 | 3 | Low pressure |  | Low pressure
489 | 3 | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII Unsigned int | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII Unsigned int
492 | 3 | Tsat corresponding to Low pressure |  | Tsat corresponding to Low pressure
495 | 3 | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
498 | 3 | DLT2 |  | DLT2
501 | 3 | Inv1 Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int | Inv1 Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
504 | 3 | Inv2 Current |  | Inv2 Current
507 | 3 | IPM T1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int | IPM T1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
510 | 3 | IPM T2 |  | IPM T2
513 | 3 | Inv1 DC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int | Inv1 DC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
516 | 3 | Inv2 DC |  | Inv2 DC
519 | 4 | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
523 | 4 | Tliq1 |  | Tliq1
527 | 4 | Tgas2 |  | Tgas2
531 | 4 | Tliq2 |  | Tliq2
535 | 4 | Tamb |  | Tamb
539 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned char | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned char
541 | 2 | Last err |  | Last err
543 | 1 | Vr | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII | Oil Temp1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
544 | 1
545 | 1
546 | 1 | Vy | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII Unsigned int | Oil Temp2 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
547 | 1
548 | 1
549 | 1 | Vb | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII Unsigned int | Suction Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
550 | 1
551 | 1
552 |  | Slave 3 Inputs |  | Slave 3 Inputs
552 | 3 | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
555 | 3 | Low pressure |  | Low pressure
558 | 3 | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII Unsigned int | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII Unsigned int
561 | 3 | Tsat corresponding to Low pressure |  | Tsat corresponding to Low pressure
564 | 3 | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
567 | 3 | DLT2 |  | DLT2
570 | 3 | Inv1 Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int | Inv1 Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
573 | 3 | Inv2 Current |  | Inv2 Current
576 | 3 | IPM T1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int | IPM T1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
579 | 3 | IPM T2 |  | IPM T2
582 | 3 | Inv1 DC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int | Inv1 DC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
585 | 3 | Inv2 DC |  | Inv2 DC
588 | 4 | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
592 | 4 | Tliq1 |  | Tliq1
596 | 4 | Tgas2 |  | Tgas2
600 | 4 | Tliq2 |  | Tliq2
604 | 4 | Tamb |  | Tamb
608 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned Char | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned Char
610 | 2 | Last err |  | Last err
612 | 1 | Vr | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII | Oil Temp1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
613 | 1
614 | 1
615 | 1 | Vy | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII Unsigned int | Oil Temp2 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
616 | 1
617 | 1
618 | 1 | Vb | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII Unsigned int | Suction Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
619 | 1
620 | 1
621 |  | Protection Master |  | Protection Master
621 | 1 | HPS | 0x30 = OFF 0x31 = ON Bool | HPS | 0x30 = OFF 0x31 = ON Bool
622 | 1 | LPS |  | LPS
623 | 1 | HP_Sw |  | HP_Sw
624 | 1 | Tc |  | Tc
625 | 1 | Te |  | Te
626 | 1 | DLT |  | DLT
627 | 1 | PR |  | Fan Motor 1 Phase Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
628 | 1 | SP
629 | 1 | Phase_Imbalance
630 | 1 | UV |  | Fan Drive 1 IPM Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
631 | 1 | OV
632 | 1 | CP1
633 | 1 | CP2 |  | Fan Drive 1 HVDC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
634 | 1 | IT1
635 | 1 | IT2
636 |  | Protection Slave 1 |  | Protection Slave 1
636 | 1 | HPS | 0x30 = OFF 0x31 = ON Bool | HPS | 0x30 = OFF 0x31 = ON Bool
637 | 1 | LPS |  | LPS
638 | 1 | HP_Sw |  | HP_Sw
639 | 1 | Tc |  | Tc
640 | 1 | Te |  | Te
641 | 1 | DLT |  | DLT
642 | 1 | PR |  | Fan Motor 1 Phase Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
643 | 1 | SP
644 | 1 | Phase_Imbalance
645 | 1 | UV |  | Fan Drive 1 IPM Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
646 | 1 | OV
647 | 1 | CP1
648 | 1 | CP2 |  | Fan Drive 1 HVDC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
649 | 1 | IT1
650 | 1 | IT2
651 |  | Protection Slave 2 |  | Protection Slave 2
651 | 1 | HPS | 0x30 = OFF 0x31 = ON Bool | HPS | 0x30 = OFF 0x31 = ON Bool
652 | 1 | LPS |  | LPS
653 | 1 | HP_Sw |  | HP_Sw
654 | 1 | Tc |  | Tc
655 | 1 | Te |  | Te
656 | 1 | DLT |  | DLT
657 | 1 | PR |  | Fan Motor 1 Phase Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
658 | 1 | SP
659 | 1 | Phase_Imbalance
660 | 1 | UV |  | Fan Drive 1 IPM Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
661 | 1 | OV
662 | 1 | CP1
663 | 1 | CP2 |  | Fan Drive 1 HVDC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
664 | 1 | IT1
665 | 1 | IT2
666 |  | Protection Slave 3 |  | Protection Slave 3
666 | 1 | HPS | 0x30 = OFF 0x31 = ON Bool | HPS | 0x30 = OFF 0x31 = ON Bool
667 | 1 | LPS |  | LPS
668 | 1 | HP_Sw |  | HP_Sw
669 | 1 | Tc |  | Tc
670 | 1 | Te |  | Te
671 | 1 | DLT |  | DLT
672 | 1 | PR |  | Fan Motor 1 Phase Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
673 | 1 | SP
674 | 1 | Phase_Imbalance
675 | 1 | UV |  | Fan Drive 1 IPM Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
676 | 1 | OV
677 | 1 | CP1
678 | 1 | CP2 |  | Fan Drive 1 HVDC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
679 | 1 | IT1
680 | 1 | IT2
681 |  | Master Pretrip Counts
681 | 1 | OC1 | (0-15)d = (0-F)h Unsigned Char | Fan Motor 2 Phase Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
682 | 1 | OC2
683 | 1 | OLL1
684 | 1 | OLL2 |  | Fan Drive 2 IPM Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
685 | 1 | OL1
686 | 1 | OL2
687 | 1 | OH1 |  | Fan Drive 2 HVDC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
688 | 1 | OH2
689 | 1 | SE1
690 | 1 | SE2 |  | Master Protections CP1, CP2, IT1, IT2 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Bit 0 : CP1 : 0 = OFF, 1= ON Bit 1 : CP2 : 0= OFF, 1= ON Bit 2 : IT1 : 0= OFF,1= ON Bit 3 : IT2 : 0= OFF, 1= ON Bit 4 to Bit 8 reserved | Bit 0 : CP1 : 0 = OFF, 1= ON Bit 1 : CP2 : 0= OFF, 1= ON Bit 2 : IT1 : 0= OFF,1= ON Bit 3 : IT2 : 0= OFF, 1= ON Bit 4 to Bit 8 reserved Example: CP1 = ON, CP2 = ON, IT1 = OFF, IT2 = ON the byte becomes: (00001011)b = (B)h. In this case, send value in ASCII as 'B'. | No
691 |  | Slave1 Pretrip Counts
691 | 1 | OC1 | (0-15)d = (0-F)h Unsigned Char | Fan Motor 2 Phase Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
692 | 1 | OC2
693 | 1 | OLL1
694 | 1 | OLL2 |  | Fan Drive 2 IPM Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
695 | 1 | OL1
696 | 1 | OL2
697 | 1 | OH1 |  | Fan Drive 2 HVDC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
698 | 1 | OH2
699 | 1 | SE1
700 | 1 | SE2 |  | Slave 1 Protections CP1, CP2, IT1, IT2 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Bit 0 : CP1 : 0 = OFF, 1= ON Bit 1 : CP2 : 0= OFF, 1= ON Bit 2 : IT1 : 0= OFF,1= ON Bit 3 : IT2 : 0= OFF, 1= ON Bit 4 to Bit 8 reserved
701 |  | Slave2 Pretrip Counts
701 | 1 | OC1 | (0-15)d = (0-F)h Unsigned Char | Fan Motor 2 Phase Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
702 | 1 | OC2
703 | 1 | OLL1
704 | 1 | OLL2 |  | Fan Drive 2 IPM Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
705 | 1 | OL1
706 | 1 | OL2
707 | 1 | OH1 |  | Fan Drive 2 HVDC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
708 | 1 | OH2
709 | 1 | SE1
710 | 1 | SE2 |  | Slave 2 Protections CP1, CP2, IT1, IT2 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Bit 0 : CP1 : 0 = OFF, 1= ON Bit 1 : CP2 : 0= OFF, 1= ON Bit 2 : IT1 : 0= OFF,1= ON Bit 3 : IT2 : 0= OFF, 1= ON Bit 4 to Bit 8 reserved
711 |  | Slave3 Pretrip Counts
711 | 1 | OC1 | (0-15)d = (0-F)h Unsigned Char | Fan Motor 2 Phase Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Receiver to convert to Decimal then divide by 10
712 | 1 | OC2
713 | 1 | OLL1
714 | 1 | OLL2 |  | Fan Drive 2 IPM Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
715 | 1 | OL1
716 | 1 | OL2
717 | 1 | OH1 |  | Fan Drive 2 HVDC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
718 | 1 | OH2
719 | 1 | SE1
720 | 1 | SE2 |  | Slave 3 Protections CP1, CP2, IT1, IT2 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int Bit 0 : CP1 : 0 = OFF, 1= ON Bit 1 : CP2 : 0= OFF, 1= ON Bit 2 : IT1 : 0= OFF,1= ON Bit 3 : IT2 : 0= OFF, 1= ON Bit 4 to Bit 8 reserved
721 | 1 | Reserved Bytes | 'X' | Master: Comp1 Oil Level (%) | Data to sent in ASCII Format ASCII- 0 to 9 & : 0=0% 1=10% . 9=90% :=100%
722 | 1 | Reserved Bytes | 'X' | Master: Comp2 Oil Level (%) | Data to sent in ASCII Format ASCII- 0 to 9 & : 0=0% 1=10% . 9=90% :=100%
723 | 1 | Reserved Bytes | 'X' | Slave1: Comp1 Oil Level (%) | Data to sent in ASCII Format ASCII- 0 to 9 & : 0=0% 1=10% . 9=90% :=100%
724 | 1 | Reserved Bytes | 'X' | Slave1: Comp2 Oil Level (%) | Data to sent in ASCII Format ASCII- 0 to 9 & : 0=0% 1=10% . 9=90% :=100%
725 | 1 | Reserved Bytes | 'X' | Slave2: Comp1 Oil Level (%) | Data to sent in ASCII Format ASCII- 0 to 9 & : 0=0% 1=10% . 9=90% :=100%
726 | 1 | Reserved Bytes | 'X' | Slave2: Comp2 Oil Level (%) | Data to sent in ASCII Format ASCII- 0 to 9 & : 0=0% 1=10% . 9=90% :=100%
727 | 1 | Reserved Bytes | 'X' | Slave3: Comp1 Oil Level (%) | Data to sent in ASCII Format ASCII- 0 to 9 & : 0=0% 1=10% . 9=90% :=100%
728 | 1 | Reserved Bytes | 'X' | Slave3: Comp2 Oil Level (%) | Data to sent in ASCII Format ASCII- 0 to 9 & : 0=0% 1=10% . 9=90% :=100%
729 | 2 | Reserved Bytes | 'X' | Master: Comp Drive 1 FW version | (01-256)d=(01-FF)h Unsigned Char
731 | 2 | Reserved Bytes | 'X' | Master: Comp Drive 2 FW version | (01-256)d=(01-FF)h Unsigned Char
733 | 2 | Reserved Bytes | 'X' | Slave1: Comp Drive 1 FW version | (01-256)d=(01-FF)h Unsigned Char
735 | 2 | Reserved Bytes | 'X' | Slave1: Comp Drive 2 FW version | (01-256)d=(01-FF)h Unsigned Char
737 | 2 | Reserved Bytes | 'X' | Slave2: Comp Drive 1 FW version | (01-256)d=(01-FF)h Unsigned Char
739 | 2 | Reserved Bytes | 'X' | Slave2: Comp Drive 2 FW version | (01-256)d=(01-FF)h Unsigned Char
741 | 2 | Reserved Bytes | 'X' | Slave3: Comp Drive 1 FW version | (01-256)d=(01-FF)h Unsigned Char
743 | 2 | Reserved Bytes | 'X' | Slave3: Comp Drive 2 FW version | (01-256)d=(01-FF)h Unsigned Char
745 | 6 | Reserved Bytes | 'X' | Reserved Bytes | 'X'
751 |  | IDU1 |  | IDU1
751 | 1 | IDU mode | 0x30=Fan 0x31=Heat 0x32=Cool 0x33=Dry Unsigned Char | IDU mode | 0x30=Fan 0x31=Heat 0x32=Cool 0x33=Dry Unsigned Char
752 | 1 | IDU status | 0x30 = OFF 0x31 = ON Bool | IDU status | 0x30 = OFF 0x31 = ON Bool
753 | 2 | IDU error code | Range:(U0-UF)=(0x55,0x30-0x55,0x46)ASCII Unsigned Char | IDU error code | Range:(U0-UF)=(0x55,0x30-0x55,0x46)ASCII Unsigned Char | The errors can be any ODU error as well other than U0-UF | No
755 | 2 | DCL | Range:(0-101)d=(0x30,0x30-0x36,0x35)ASCII Unsigned Char | DCL | Range:(0-101)d=(0x30,0x30-0x36,0x35)ASCII Unsigned Char
757 | 3 | DeltaT | 1 byte for polarity ‘+’ = Positive ‘-‘ = Negative 2 bytes for Value Decimal range 0.0 to 5.0 (give dec point frm pc by/10) For communication range is 0 to 50 (0x30,0x30-0x33,0x32)ASCII 1st Byte sign 3 Bytes Unsigned Int | DeltaT | 1 byte for polarity ‘+’ = Positive ‘-‘ = Negative 2 bytes for Value Decimal range 0.0 to 5.0 (give dec point frm pc by/10) For communication range is 0 to 50 (0x30,0x30-0x33,0x32)ASCII 1st Byte sign 3 Bytes Unsigned Int
760 | 4 | Troom | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | Troom | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
764 | 4 | Tliq | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | Tliq | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
768 | 1 | IDU capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw 0x4C = 'L' = 44.0Kw 0x4D = 'M' = 52.7Kw 0x4E = 'N' = 70.3Kw 0x4F = 'O' = 87.9Kw 0x50 = 'P' = 105.5Kw | IDU capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw 0x4C = 'L' = 44.0Kw 0x4D = 'M' = 52.7Kw 0x4E = 'N' = 70.3Kw 0x4F = 'O' = 87.9Kw 0x50 = 'P' = 105.5Kw | missing : 0x51 = 'Q' = 122.5Kw | No
769 | 1 | Model name | 0x31 = HiWall 2TR 0x32 = Ducted 0x33 = 4Way 0x34 = Mini 4Way 0x35 = Ceiling Concealed 0x36 = Floor 0x37 = TFA 0x38 = Heat Recovery 0x39 = HiWall 1.5TR | Model name | 1 - Hiwall 2 - Ducted 3 - 4 way large cst 4 - compact 5 - ceiling concealed 6 - floor mount 7 - TFA 8 - Heat recovery 9 - One way A - 2 way cst
770 | 4 | Tsupply | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | Tsupply | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
774 | 4 | Tgas |  | Tgas
778 | 1 | Thermostat on/off | 0x30 = OFF 0x31 = ON Bool | Thermostat on/off | 0x30 = OFF 0x31 = ON Bool
779 | 1 | Set Fan Speed by ODU | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H 0x35 = Free Unsigned Char | Set Fan Speed by ODU | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H 0x35 = Free Unsigned Char
780 | 1 | Actual Fan Speed |  | Actual Fan Speed
781 | 2 | user set | Range: (0-30)d=(0x30,0x30-0x31,0x45)ASCII Unsigned Char | user set | Range: (0-30)d=(0x30,0x30-0x31,0x45)ASCII Unsigned Char
783 | 1 | pump on/off | 0x30 = OFF 0x31 = ON Bool | pump on/off | 0x30 = OFF 0x31 = ON Bool
784 | 1 | flap position | 0x30 = Swing 0x31 = F1 0x32 = F2 0x33 = F3 0x34 = F4 0x35 = F5 Unsigned Char | flap position | 0x30 = Swing 0x31 = F1 0x32 = F2 0x33 = F3 0x34 = F4 0x35 = F5 Unsigned Char
785 | 1 | swing on/off | 0x30 = OFF 0x31 = ON Bool | swing on/off | 0x30 = OFF 0x31 = ON Bool
786 | 5 | EXV step of IDU | Decimal Range : -520 to 520 Total 5bytes1 for polarity +’ = Positive ‘-‘ = Negative 'a' = absolute And4 bytes for value Range:(0 to520)d=(0-208)h (0x30x30,0x30,0x30 – 0x32,0x30,0x38)ASCII 1st Byte sign 4 Bytes Unsigned Int | EXV step of IDU | Decimal Range : -520 to 520 Total 5bytes1 for polarity +’ = Positive ‘-‘ = Negative 'a' = absolute And4 bytes for value Range:(0 to520)d=(0-208)h (0x30x30,0x30,0x30 – 0x32,0x30,0x38)ASCII 1st Byte sign 4 Bytes Unsigned Int
791 | 4 | delta Tcoil | Decimal range: -20.0 to 30.0 °C with resolution of 0.5 Total 4 bytes1 byte for polarity‘ +’ = Positive ‘-‘ = Negative And3 bytes for value Range: 0.0 to 30.0 (0 to 300)d=(0-12C)h (0x30,0x30,0x30 to 0x31,0x32,0x43)ASCII 1st Byte sign 3 Bytes Unsigned Int | delta Tcoil | Decimal range: -20.0 to 30.0 °C with resolution of 0.5 Total 4 bytes1 byte for polarity‘ +’ = Positive ‘-‘ = Negative And3 bytes for value Range: 0.0 to 30.0 (0 to 300)d=(0-12C)h (0x30,0x30,0x30 to 0x31,0x32,0x43)ASCII 1st Byte sign 3 Bytes Unsigned Int
795 | 1 | Set Fan Speed By IDU | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 = M 0x34 = H 0x35 = Free Unsigned Char | Set Fan Speed By IDU | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 = M 0x34 = H 0x35 = Free Unsigned Char
796 | 1 | IDU 1 min OFF | 0x30 = OFF 0x31 = ON Bool | IDU 1 min OFF | 0x30 = OFF 0x31 = ON Bool
797 | 1 | Door Key Status |  | Door Key Status
798 | 2 | IDU Program Version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char | IDU Program Version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
800 | 1 | IDU on Lock | 0x30 = Unlocked 0x31 = Locked Bool | IDU on Lock | 0x30 = Unlocked 0x31 = Locked Bool
801 | 1 | IDU off Lock | 0x30 = Unlocked 0x31 = Locked Bool | IDU off Lock | 0x30 = Unlocked 0x31 = Locked Bool
802 | 1 | IDU Mode Lock | 0x30 = Unlocked 0x31 = Locked Bool | IDU Mode Lock | 0x30 = Unlocked 0x31 = Locked Bool
803 | 1 | IDU Temp Lock | 0x30 = Unlocked 0x31 = Locked Bool | IDU Temp Lock | 0x30 = Unlocked 0x31 = Locked Bool
804 | 4 | Start Time | 2Byte for Hour 2Byte for Minute Unsigned int | Start Time | 2Byte for Hour 2Byte for Minute Unsigned int
808 | 4 | End Time | 2Byte for Hour 2Byte for Minute Unsigned int | End Time | 2Byte for Hour 2Byte for Minute Unsigned int
812 | 1 | Sleep Mode | 0x30 = OFF 0x31 = ON Bool | Sleep Mode | 0x30 = OFF 0x31 = ON Bool
813 | 1 | Drain Pump Lock | 0x30 = Unlocked 0x31 = Locked Bool | Drain Pump Lock | 0x30 = Unlocked 0x31 = Locked Bool
814 | 1 | Door Key Lock | 0x30 = Unlocked 0x31 = Locked Bool | Door Key Lock | 0x30 = Unlocked 0x31 = Locked Bool
815 | 1 | IDU Future bytes | 'X' | IDU Future bytes | 'X'
816
816 | 65 | IDU2 | All 63 Bytes are same as IDU1 | IDU2 | All 63 Bytes are same as IDU1
881 | 65 | IDU3 |  | IDU3
946 | 65 | IDU4 |  | IDU4
1011 | 65 | IDU5 |  | IDU5
1076 | 65 | IDU6 |  | IDU6
1141 | 65 | IDU7 |  | IDU7
1206 | 65 | IDU8 |  | IDU8
1271 | 65 | IDU9 |  | IDU9
1336 | 65 | IDU10 |  | IDU10
1401 | 65 | IDU11 |  | IDU11
1466 | 65 | IDU12 |  | IDU12
1531 | 65 | IDU13 |  | IDU13
1596 | 65 | IDU14 |  | IDU14
1661 | 65 | IDU15 |  | IDU15
1726 | 65 | IDU16 |  | IDU16
1791 | 65 | IDU17 |  | IDU17
1856 | 65 | IDU18 |  | IDU18
1921 | 65 | IDU19 |  | IDU19
1986 | 65 | IDU20 |  | IDU20
2051 | 65 | IDU21 |  | IDU21
2116 | 65 | IDU22 |  | IDU22
2181 | 65 | IDU23 |  | IDU23
2246 | 65 | IDU24 |  | IDU24
2311 | 65 | IDU25 |  | IDU25
2376 | 65 | IDU26 |  | IDU26
2441 | 65 | IDU27 |  | IDU27
2506 | 65 | IDU28 |  | IDU28
2571 | 65 | IDU29 |  | IDU29
2636 | 65 | IDU30 |  | IDU30
2701 | 65 | IDU31 |  | IDU31
2766 | 65 | IDU32 |  | IDU32
2831 | 65 | IDU33 |  | IDU33
2896 | 65 | IDU34 |  | IDU34
2961 | 65 | IDU35 |  | IDU35
3026 | 65 | IDU36 |  | IDU36
3091 | 65 | IDU37 |  | IDU37
3156 | 65 | IDU38 |  | IDU38
3221 | 65 | IDU39 |  | IDU39
3286 | 65 | IDU40 |  | IDU40
3351 | 65 | IDU41 |  | IDU41
3416 | 65 | IDU42 |  | IDU42
3481 | 65 | IDU43 |  | IDU43
3546 | 65 | IDU44 |  | IDU44
3611 | 65 | IDU45 |  | IDU45
3676 | 65 | IDU46 |  | IDU46
3741 | 65 | IDU47 |  | IDU47
3806 | 65 | IDU48 |  | IDU48
3871 | 65 | IDU49 |  | IDU49
3936 | 65 | IDU50 |  | IDU50
4001 | 65 | IDU51 |  | IDU51
4066 | 65 | IDU52 |  | IDU52
4131 | 65 | IDU53 |  | IDU53
4196 | 65 | IDU54 |  | IDU54
4261 | 65 | IDU55 |  | IDU55
4326 | 65 | IDU56 |  | IDU56
4391 | 65 | IDU57 |  | IDU57
4456 | 65 | IDU58 |  | IDU58
4521 | 65 | IDU59 |  | IDU59
4586 | 65 | IDU60 |  | IDU60
4651 | 65 | IDU61 |  | IDU61
4716 | 65 | IDU62 |  | IDU62
4781 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII Unsigned Char | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII Unsigned Char
4783 | 1 | Data Type | For Engineering data 'E' = 0x45 For User data 'U' = 0x55 | Data Type | For Engineering data 'E' = 0x45 For User data 'U' = 0x55
4784 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII Unsigned Char | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII Unsigned Char
4786 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission Unsigned int | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission Unsigned int
4790 | 1 | # | End of Data | # | End of Data
4791 | Total No of Bytes

## IVRF User Frame
Command Frame From PC Monitoring to ODU Master of System for User Data
* ¦ P¦ C ¦ Frame Count ¦ Syatem ID ¦ Command ¦ Data Type(U) ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | C | Command Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C
5 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
7 | 2 | Command | For System Status Data 01d=(01)h=(0x30,0x31)ASCII
9 | 1 | Data Type | For User data 'U' = 0x55
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17
Reply Send from ODU Master of System to PC Monitoring for User Data
* ¦ M¦ D ¦ XXI ¦ System Data ¦ Syatem ID¦ Data Type(U) ¦ Protocol Version no ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame From Master to PC monitoring
2 | 1 | D | Data Frame
3 | 3 | XXI | IVRF
6 |  | Master Inputs
6 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
7 | 4 | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
11 |  | Slave 1 Inputs
11 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
12 | 4 | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
16 |  | Slave 2 Inputs
16 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
17 | 4 | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
21 |  | Slave 3 Inputs
21 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
22 | 4 | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
26 |  | Master Output
26 | 1 | Fix1 | 0x30 = OFF 0x31 = ON Bool
27 | 1 | Fix2
28 |  | Slave 1 Output
28 | 1 | Fix1 | 0x30 = OFF 0x31 = ON Bool
29 | 1 | Fix2
30 |  | Slave 2 Output
30 | 1 | Fix1 | 0x30 = OFF 0x31 = ON Bool
31 | 1 | Fix2
32 |  | Slave 3 Output
32 | 1 | Fix1 | 0x30 = OFF 0x31 = ON Bool
33 | 1 | Fix2
34 |  | System Info
34 | 2 | IDUqty | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned char
36 | 3 | SUMkw ODU | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII Unsigned int
39 | 4 | SUMkw IDU | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
43 | 3 | Diversity | Range:(0-150)d=(provision for 0-999)d= (0x30,0x30,0x30-0x33,0x45,0x37)ASCII Unsigned int
46 | 1 | ODU Mode | 0x30 = Off 0x31 = Heat 0x32 = Cool 0x33 = Free Unsigned Char
47 |  | General Info Master
47 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned char
49 | 2 | Last err
51 |  | General Info Slave 1
51 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned char
53 | 2 | Last err
55 |  | General Info Slave 2
55 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned char
57 | 2 | Last err
59 |  | General Info Slave 3
59 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned char
61 | 2 | Last err
63 | 1 | No of Slaves | 0x31 = 1 0x32 = 2 0x33 = 3 Unsigned char
64 | 4 | ODU Future bytes | 'X'
68 |  | IDU1
68 | 1 | IDU mode | 0x30=Fan 0x31=Heat 0x32=Cool 0x33=Dry Unsigned char | 0
69 | 1 | IDU status | 0x30 = OFF 0x31 = ON Bool | 1
70 | 2 | IDU error code | Range:(U0-UF)=(0x55,0x30-0x55,0x46)ASCII Unsigned char | 2
72 | 4 | Troom | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | 4
76 | 1 | IDU capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw 0x4C = 'L' = 44.0Kw 0x4D = 'M' = 52.7Kw 0x4E = 'N' = 70.3Kw 0x4F = 'O' = 87.9Kw 0x50 = 'P' = 105.5Kw Unsigned char | 8
77 | 1 | Model name | 1 - Hiwall 2 - Ducted 3 - 4 way large cst 4 - compact 5 - ceiling concealed 6 - floor mount 7 - TFA 8 - Heat recovery 9 - One way A - 2 way cst | 9
78 | 1 | Set Fan Speed | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H 0x35 = Free Unsigned char | 10
79 | 2 | user set | Range: (0-30)d=(0x30,0x30-0x31,0x45)ASCII Unsigned char | 11
81 | 1 | flap position | 0x30 = Swing 0x31 = F1 0x32 = F2 0x33 = F3 0x34 = F4 0x35 = F5 Unsigned char | 13
82 | 1 | IDU on Lock | 0x30 = Unlocked 0x31 = Locked Bool | 14
83 | 1 | IDU off Lock | 0x30 = Unlocked 0x31 = Locked Bool | 15
84 | 1 | IDU Mode Lock | 0x30 = Unlocked 0x31 = Locked Bool | 16
85 | 1 | IDU Temp Lock | 0x30 = Unlocked 0x31 = Locked Bool | 17
86 | 4 | Start Time | 2Byte for Hour 2Byte for Minute Unsigned int | 18
90 | 4 | End Time | 2Byte for Hour 2Byte for Minute Unsigned int | 22
94 | 1 | Sleep Mode | 0x30 = OFF 0x31 = ON Bool | 26
95 | 1 | IDU Future bytes | 'X' | 27
96 |  |  |  | 28
96 | 28 | IDU2 | All 28 Bytes are same as IDU1
124 | 28 | IDU3
152 | 28 | IDU4
180 | 28 | IDU5
208 | 28 | IDU6
236 | 28 | IDU7
264 | 28 | IDU8
292 | 28 | IDU9
320 | 28 | IDU10
348 | 28 | IDU11
376 | 28 | IDU12
404 | 28 | IDU13
432 | 28 | IDU14
460 | 28 | IDU15
488 | 28 | IDU16
516 | 28 | IDU17
544 | 28 | IDU18
572 | 28 | IDU19
600 | 28 | IDU20
628 | 28 | IDU21
656 | 28 | IDU22
684 | 28 | IDU23
712 | 28 | IDU24
740 | 28 | IDU25
768 | 28 | IDU26
796 | 28 | IDU27
824 | 28 | IDU28
852 | 28 | IDU29
880 | 28 | IDU30
908 | 28 | IDU31
936 | 28 | IDU32
964 | 28 | IDU33
992 | 28 | IDU34
1020 | 28 | IDU35
1048 | 28 | IDU36
1076 | 28 | IDU37
1104 | 28 | IDU38
1132 | 28 | IDU39
1160 | 28 | IDU40
1188 | 28 | IDU41
1216 | 28 | IDU42
1244 | 28 | IDU43
1272 | 28 | IDU44
1300 | 28 | IDU45
1328 | 28 | IDU46
1356 | 28 | IDU47
1384 | 28 | IDU48
1412 | 28 | IDU49
1440 | 28 | IDU50
1468 | 28 | IDU51
1496 | 28 | IDU52
1524 | 28 | IDU53
1552 | 28 | IDU54
1580 | 28 | IDU55
1608 | 28 | IDU56
1636 | 28 | IDU57
1664 | 28 | IDU58
1692 | 28 | IDU59
1720 | 28 | IDU60
1748 | 28 | IDU61
1776 | 28 | IDU62
1804 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII Unsigned char
1806 | 1 | Data Type = U | For Engineering data 'E' = 0x45 For User data 'U' = 0x55
1807 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII Unsigned char
1809 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission Unsigned int
1813 | 1 | # | End of Data
1814 | Total No of Bytes

## IVRF ODU Parameters
|  |  |  | Issues or changes | ODU Firmware change required?
Frame From PC Monitoring to ODU Masters for ODU Parameters
* ¦ P¦ B ¦ Frame Count ¦ Data ¦ Protocol Version ¦ CRC¦ #
NOTE: 1. for Slave1 & Slave2, 1) PERF, 2)CHKM , 3)SLTM , 4)SLTL , 5)DMDL parameters are not used. So, keep these parameter text boxes disabled in PC software. And send 0x30 for above parameters in protocol bytes which will be ignored while data processing at Slave ODU. 2. By default, mode selection for every parameter is Auto.
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | B | Broadcast Frame
3 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 8B
6 | 1 | O | O=ODU
7 | 1 | P | P=Parameters
8 | 1 | System1 | If Bit=1 then ODU State=Active If Bit=0 then ODU State=Inactive Bit 0-> ODUm State Bit 1-> Slave1 State Bit 2-> Slave2 State Bit 3-> 0 e.g. if ODUm & Slave2 Active then D1=0x05 D1=0x35(ASCII)
9 | 1 | System2 | Bit 0-> ODUm State Bit 1-> Slave1 State Bit 2-> Slave2 State Bit 3-> 0
10 | 1 | System3
11 | 1 | System4
12 | 1 | System5
13 | 1 | System6
14 | 1 | System7
15 | 1 | System8
16 | 1 | System9
17 | 1 | System10
18 | 1 | System11
19 | 1 | System12
20 | 1 | System13
21 | 1 | System14
22 | 1 | System15
23 | 1 | System16
24 | 1 | System17
25 | 1 | System18
26 | 1 | System19
27 | 1 | System20
28 | 1 | System21
29 | 1 | System22
30 | 1 | System23
31 | 1 | System24
32 | 1 | System25
33 | 1 | System26
34 | 1 | System27
35 | 1 | System28
36 | 1 | System29
37 | 1 | System30
38 | 1 | System31
39 | 1 | System32
40 | 1 | System33
41 | 1 | System34
42 | 1 | System35
43 | 1 | System36
44 | 1 | System37
45 | 1 | System38
46 | 1 | System39
47 | 1 | System40
48 | 1 | System41
49 | 1 | System42
50 | 1 | System43
51 | 1 | System44
52 | 1 | System45
53 | 1 | System46
54 | 1 | System47
55 | 1 | System48
56 | 1 | System49
57 | 1 | System50
58 | 1 | System51
59 | 1 | System52
60 | 1 | System53
61 | 1 | System54
62 | 1 | System55
63 | 1 | System56
64 | 1 | System57
65 | 1 | System58
66 | 1 | System59
67 | 1 | System60
68 | 3 | Set RPS | to Set 80 RPS for INV 1, Set RPS = 180 to Set 80 RPS for INV 2, Set RPS = 280 to Set 80 RPS for INV 1 and INV2, Set RPS = 380 to Set 80 RPS for INV1 and 0 RPS for INV2, Set RPS = 480 | To set Auto mode for INV 1, Set RPS = 1 To set Auto mode for INV 2, Set RPS = 2 To set Auto mode for INV 1 and INV 2, Set RPS = (500-999) to Set 80 RPS for INV 1, Set RPS = 180 to Set 80 RPS for INV 2, Set RPS = 280 to Set 80 RPS for INV 1 and INV2, Set RPS = 380 to Set 80 RPS for INV1 and 0 RPS for INV2, Set RPS = 480 | No
71 | 1 | RPS Mode | 0x30 = Auto,0x31 = Manual
72 | 1 | SV6 | 0x30 = OFF 0x31 = ON
73 | 1 | SV6 Mode | 0x30 = Auto,0x31 = Manual
74 | 1 | SV7 | 0x30 = OFF 0x31 = ON
75 | 1 | SV7 Mode | 0x30 = Auto,0x31 = Manual
76 | 1 | 4W V | 0x30 = OFF 0x31 = ON
77 | 1 | 4W V Mode | 0x30 = Auto,0x31 = Manual
78 | 1 | SORV | 0x30 = OFF 0x31 = ON
79 | 1 | SORV Mode | 0x30 = Auto,0x31 = Manual
80 | 1 | OPOV | 0x30 = OFF 0x31 = ON
81 | 1 | OPOV Mode | 0x30 = Auto,0x31 = Manual
82 | 1 | ORCV | 0x30 = OFF 0x31 = ON
83 | 1 | ORCV Mode | 0x30 = Auto,0x31 = Manual
84 | 1 | LIBA | 0x30 = OFF 0x31 = ON
85 | 1 | LIBA Mode | 0x30 = Auto,0x31 = Manual
86 | 1 | LIA1 | 0x30 = OFF 0x31 = ON
87 | 1 | LIA1 Mode | 0x30 = Auto,0x31 = Manual
88 | 1 | Reserved
89 | 1 | Reserved
90 | 1 | Commissioning Mode | 0x30 = OFF 0x31 = ON
91 | 1 | Commissioning Mode Mode | 0x30 = Auto,0x31 = Manual
92 | 1 | MLQV | 0x30 = OFF 0x31 = ON
93 | 1 | MLQV Mode | 0x30 = Auto,0x31 = Manual
94 | 1 | HOTD | 0x30 = OFF 0x31 = ON
95 | 1 | HOTD Mode | 0x30 = Auto,0x31 = Manual
96 | 3 | EXV 1 | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII | Range required (0-3000)d | No
99 | 1 | EXV 1 Mode
100 | 2 | IDUqty | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII
102 | 1 | IDUqty Mode | 0x30 = Auto,0x31 = Manual
103 | 1 | PERF | 0x30 = OFF 0x31 = ON
104 | 1 | PERF Mode | 0x30 = Auto,0x31 = Manual
105 | 1 | CHKM | 0x30 = OFF 0x31 = ON
106 | 1 | CHKM Mode | 0x30 = Auto,0x31 = Manual
107 | 1 | SLT DMD Mode | 0x30 = Auto,0x31 = Manual
108 | 1 | SLT / DMD | 0x30 = SLT,0x31 = DMD
109 | 1 | SLT / DMD Active | 0x30 = Disable 0x31 = ON for 24 Hours 0x32 = Starts for 9 Hours from SLT/DMD Time
110 | 2 | SLT / DMD Time | 00H to 17H i.e 00 to 23 Hours
112 | 1 | SLT / DMD Level | For Silent Mode - 0x30 = Low 0x31 = High For Demand Mode - 0x30 = 75% Demand Level 0 0x31 = 50% Demand Level 1 0x32 = 25% Demand Level 2 0x33 = 0% Demand Level 3
113 | 1 | Reserved
114 | 1 | Reserved
115 | 1 | ODU Test MODE | 0x30 = OFF,0x31 = ON
116 | 2 | FanSp | Range: (0=11)d=(0-B)h=(0x30,0x42)ASCII | Range should be (0-12) | No
118 | 1 | FanSp Mode | 0x30 = Auto,0x31 = Manual
119 | 8 | Set Date | Byte1 = D Byte2 = D Byte3 = M Byte4 = M Byte5 = Y Byte6 = Y Byte7 = Y Byte8 = Y
127 | 1 | Set Date Mode | 0x30 = Auto,0x31 = Manual
128 | 6 | Set Time | Byte1 = H Byte2 = H Byte3 = M Byte4 = M Byte5 = S Byte6 = S
134 | 1 | Set Time Mode | 0x30 = Auto,0x31 = Manual
135 | 3 | EXV 2 | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII | Range required (0-3000)d | No
138 | 1 | EXV 2 Mode
139 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
143 | 1 | # | End of Data
144 | Total No of Bytes

## IVRF ODU Parameters 147 bytes
|  |  |  | Issues or changes | ODU Firmware change required?
Frame From PC Monitoring to ODU Masters for ODU Parameters
* ¦ P¦ B ¦ Frame Count ¦ Data ¦ Protocol Version ¦ CRC¦ #
NOTE: 1. for Slave1 & Slave2, 1) PERF, 2)CHKM , 3)SLTM , 4)SLTL , 5)DMDL parameters are not used. So, keep these parameter text boxes disabled in PC software. And send 0x30 for above parameters in protocol bytes which will be ignored while data processing at Slave ODU. 2. By default, mode selection for every parameter is Auto. 3. The IVRF ODU Parameters should be of length 147 bytes. It is implemented in IVRF 4+, IVRF 5+, IVRF 6th Gen and it is also implemented in Service tool.
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | B | Broadcast Frame
3 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 8E
6 | 1 | O | O=ODU
7 | 1 | P | P=Parameters
8 | 1 | System1 | If Bit=1 then ODU State=Active If Bit=0 then ODU State=Inactive Bit 0-> ODUm State Bit 1-> Slave1 State Bit 2-> Slave2 State Bit 3-> 0 e.g. if ODUm & Slave2 Active then D1=0x05 D1=0x35(ASCII)
9 | 1 | System2 | Bit 0-> ODUm State Bit 1-> Slave1 State Bit 2-> Slave2 State Bit 3-> 0
10 | 1 | System3
11 | 1 | System4
12 | 1 | System5
13 | 1 | System6
14 | 1 | System7
15 | 1 | System8
16 | 1 | System9
17 | 1 | System10
18 | 1 | System11
19 | 1 | System12
20 | 1 | System13
21 | 1 | System14
22 | 1 | System15
23 | 1 | System16
24 | 1 | System17
25 | 1 | System18
26 | 1 | System19
27 | 1 | System20
28 | 1 | System21
29 | 1 | System22
30 | 1 | System23
31 | 1 | System24
32 | 1 | System25
33 | 1 | System26
34 | 1 | System27
35 | 1 | System28
36 | 1 | System29
37 | 1 | System30
38 | 1 | System31
39 | 1 | System32
40 | 1 | System33
41 | 1 | System34
42 | 1 | System35
43 | 1 | System36
44 | 1 | System37
45 | 1 | System38
46 | 1 | System39
47 | 1 | System40
48 | 1 | System41
49 | 1 | System42
50 | 1 | System43
51 | 1 | System44
52 | 1 | System45
53 | 1 | System46
54 | 1 | System47
55 | 1 | System48
56 | 1 | System49
57 | 1 | System50
58 | 1 | System51
59 | 1 | System52
60 | 1 | System53
61 | 1 | System54
62 | 1 | System55
63 | 1 | System56
64 | 1 | System57
65 | 1 | System58
66 | 1 | System59
67 | 1 | System60
68 | 3 | Set RPS | to Set 80 RPS for INV 1, Set RPS = 180 to Set 80 RPS for INV 2, Set RPS = 280 to Set 80 RPS for INV 1 and INV2, Set RPS = 380 to Set 80 RPS for INV1 and 0 RPS for INV2, Set RPS = 480 | To set Auto mode for INV 1, Set RPS = 1 To set Auto mode for INV 2, Set RPS = 2 To set Auto mode for INV 1 and INV 2, Set RPS = (500-999) to Set 80 RPS for INV 1, Set RPS = 180 to Set 80 RPS for INV 2, Set RPS = 280 to Set 80 RPS for INV 1 and INV2, Set RPS = 380 to Set 80 RPS for INV1 and 0 RPS for INV2, Set RPS = 480 | No
71 | 1 | RPS Mode | 0x30 = Auto,0x31 = Manual
72 | 1 | SV6 | 0x30 = OFF 0x31 = ON
73 | 1 | SV6 Mode | 0x30 = Auto,0x31 = Manual
74 | 1 | SV7 | 0x30 = OFF 0x31 = ON
75 | 1 | SV7 Mode | 0x30 = Auto,0x31 = Manual
76 | 1 | 4W V | 0x30 = OFF 0x31 = ON
77 | 1 | 4W V Mode | 0x30 = Auto,0x31 = Manual
78 | 1 | SORV | 0x30 = OFF 0x31 = ON
79 | 1 | SORV Mode | 0x30 = Auto,0x31 = Manual
80 | 1 | OPOV | 0x30 = OFF 0x31 = ON
81 | 1 | OPOV Mode | 0x30 = Auto,0x31 = Manual
82 | 1 | ORCV | 0x30 = OFF 0x31 = ON
83 | 1 | ORCV Mode | 0x30 = Auto,0x31 = Manual
84 | 1 | LIBA | 0x30 = OFF 0x31 = ON
85 | 1 | LIBA Mode | 0x30 = Auto,0x31 = Manual
86 | 1 | LIA1 | 0x30 = OFF 0x31 = ON
87 | 1 | LIA1 Mode | 0x30 = Auto,0x31 = Manual
88 | 1 | Reserved
89 | 1 | Reserved
90 | 1 | Commissioning Mode | 0x30 = OFF 0x31 = ON
91 | 1 | Commissioning Mode Mode | 0x30 = Auto,0x31 = Manual
92 | 1 | MLQV | 0x30 = OFF 0x31 = ON
93 | 1 | MLQV Mode | 0x30 = Auto,0x31 = Manual
94 | 1 | HOTD | 0x30 = OFF 0x31 = ON
95 | 1 | HOTD Mode | 0x30 = Auto,0x31 = Manual
96 | 3 | EXV 1 | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII | Range required (0-3000)d | No
99 | 1 | EXV 1 Mode
100 | 2 | IDUqty | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII
102 | 1 | IDUqty Mode | 0x30 = Auto,0x31 = Manual
103 | 1 | PERF | 0x30 = OFF 0x31 = ON
104 | 1 | PERF Mode | 0x30 = Auto,0x31 = Manual
105 | 1 | CHKM | 0x30 = OFF 0x31 = ON
106 | 1 | CHKM Mode | 0x30 = Auto,0x31 = Manual
107 | 1 | SLT DMD Mode | 0x30 = Auto,0x31 = Manual
108 | 1 | SLT / DMD | 0x30 = SLT,0x31 = DMD
109 | 1 | SLT / DMD Active | 0x30 = Disable 0x31 = ON for 24 Hours 0x32 = Starts for 9 Hours from SLT/DMD Time
110 | 2 | SLT / DMD Time | 00H to 17H i.e 00 to 23 Hours
112 | 1 | SLT / DMD Level | For Silent Mode - 0x30 = Low 0x31 = High For Demand Mode - 0x30 = 75% Demand Level 0 0x31 = 50% Demand Level 1 0x32 = 25% Demand Level 2 0x33 = 0% Demand Level 3
113 | 1 | Reserved
114 | 1 | ODU Test MODE | 0x30 = OFF,0x31 = ON
115 | 2 | FanSp | Range: (0=11)d=(0-B)h=(0x30,0x42)ASCII | Range should be (0-12) | No
117 | 1 | FanSp Mode | 0x30 = Auto,0x31 = Manual
118 | 8 | Set Date | Byte1 = D Byte2 = D Byte3 = M Byte4 = M Byte5 = Y Byte6 = Y Byte7 = Y Byte8 = Y
126 | 1 | Set Date Mode | 0x30 = Auto,0x31 = Manual
127 | 6 | Set Time | Byte1 = H Byte2 = H Byte3 = M Byte4 = M Byte5 = S Byte6 = S
133 | 1 | Set Time Mode | 0x30 = Auto,0x31 = Manual
134 | 3 | EXV 2 | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII | Range required (0-3000)d | No
137 | 1 | EXV 2 Mode
138 | 1 | Commissioning Mode | 0x30 = OFF 0x31 = ON
139 | 1 | Commissioning Mode Mode | 0x30 = Auto,0x31 = Manual
140 | 1 | Reserved
141 | 1 | Reserved
142 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
146 | 1 | # | End of Data
147 | Total No of Bytes

## IDU Parameters
|  |  |  | Issues or changes | ODU Firmware change required?
Frame From PC Monitoring to ODU Master for IDU Parameters
* ¦ P¦ B ¦ Frame Count ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | B | Broadcast Frame
3 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 4A9
6 | 1 | I | I = IDU = 0x49
7 | 1 | P | P = Parameters = 0x50
8 | 1 | System Identifier | S
9 | 2 | System1 ID | (01)d=(01h)=(0x30,0x31)
11 | 2 | IDU1 to IDU8 | If Bit=1 then IDU State=Active If Bit=0 then IDU State=Inactive Bit 0-> IDU1 State Bit 1-> IDU2 State Bit 2-> IDU3 State Bit 3-> IDU4 State Bit 4-> IDU5 State Bit 5-> IDU6 State Bit 6-> IDU7 State Bit 7-> IDU8 State e.g. if IDU 1,4,5 & 8 are Active then Byte=0x99 99h=0x39,0x39 (ASCII) D4=0x39 D5=0x39
13 | 2 | IDU9 to IDU16 | Bit 0-> IDU9 State Bit 1-> IDU10 State Bit 2-> IDU11State Bit 3-> IDU12 State Bit 4-> IDU13 State Bit 5-> IDU14 State Bit 6-> IDU15 State Bit 7-> IDU16 State
15 | 2 | IDU17 to IDU24 | Bit 0-> IDU17 State Bit 1-> IDU18 State Bit 2-> IDU19State Bit 3-> IDU20 State Bit 4-> IDU21 State Bit 5-> IDU22 State Bit 6-> IDU23 State Bit 7-> IDU24 State
17 | 2 | IDU25 to IDU32 | Bit 0-> IDU25 State Bit 1-> IDU26 State Bit 2-> IDU27State Bit 3-> IDU28 State Bit 4-> IDU29 State Bit 5-> IDU30 State Bit 6-> IDU31 State Bit 7-> IDU32 State
19 | 2 | IDU33 to IDU40 | Bit 0-> IDU33 State Bit 1-> IDU34 State Bit 2-> IDU35State Bit 3-> IDU36 State Bit 4-> IDU37 State Bit 5-> IDU38 State Bit 6-> IDU39 State Bit 7-> IDU40 State
21 | 2 | IDU41 to IDU48 | Bit 0-> IDU41 State Bit 1-> IDU42 State Bit 2-> IDU43State Bit 3-> IDU44 State Bit 4-> IDU45 State Bit 5-> IDU46 State Bit 6-> IDU47 State Bit 7-> IDU48 State
23 | 2 | IDU49 to IDU56 | Bit 0-> IDU49 State Bit 1-> IDU50 State Bit 2-> IDU51State Bit 3-> IDU52 State Bit 4-> IDU53 State Bit 5-> IDU54 State Bit 6-> IDU55 State Bit 7-> IDU56 State
25 | 2 | IDU57 to IDU62 | Bit 0-> IDU57 State Bit 1-> IDU58 State Bit 2-> IDU59State Bit 3-> IDU60 State Bit 4-> IDU61 State Bit 5-> IDU62 State Bit 6-> X -Don’t care Bit 7-> X -Don’t care
27 | 19 | System2 | System ID = 02
46 | 19 | System3 | System ID = 03
65 | 19 | System4 | System ID = 04
84 | 19 | System5 | System ID = 05
103 | 19 | System6 | System ID = 06
122 | 19 | System7 | System ID = 07
141 | 19 | System8 | System ID = 08
160 | 19 | System9 | System ID = 09
179 | 19 | System10 | System ID = 10
198 | 19 | System11 | System ID = 11
217 | 19 | System12 | System ID = 12
236 | 19 | System13 | System ID = 13
255 | 19 | System14 | System ID = 14
274 | 19 | System15 | System ID = 15
293 | 19 | System16 | System ID = 16
312 | 19 | System17 | System ID = 17
331 | 19 | System18 | System ID = 18
350 | 19 | System19 | System ID = 19
369 | 19 | System20 | System ID = 20
388 | 19 | System21 | System ID = 21
407 | 19 | System22 | System ID = 22
426 | 19 | System23 | System ID = 23
445 | 19 | System24 | System ID = 24
464 | 19 | System25 | System ID = 25
483 | 19 | System26 | System ID = 26
502 | 19 | System27 | System ID = 27
521 | 19 | System28 | System ID = 28
540 | 19 | System29 | System ID = 29
559 | 19 | System30 | System ID = 30
578 | 19 | System31 | System ID = 31
597 | 19 | System32 | System ID = 32
616 | 19 | System33 | System ID = 33
635 | 19 | System34 | System ID = 34
654 | 19 | System35 | System ID = 35
673 | 19 | System36 | System ID = 36
692 | 19 | System37 | System ID = 37
711 | 19 | System38 | System ID = 38
730 | 19 | System39 | System ID = 39
749 | 19 | System40 | System ID = 40
768 | 19 | System41 | System ID = 41
787 | 19 | System42 | System ID = 42
806 | 19 | System43 | System ID = 43
825 | 19 | System44 | System ID = 44
844 | 19 | System45 | System ID = 45
863 | 19 | System46 | System ID = 46
882 | 19 | System47 | System ID = 47
901 | 19 | System48 | System ID = 48
920 | 19 | System49 | System ID = 49
939 | 19 | System50 | System ID = 50
958 | 19 | System51 | System ID = 51
977 | 19 | System52 | System ID = 52
996 | 19 | System53 | System ID = 53
1015 | 19 | System54 | System ID = 54
1034 | 19 | System55 | System ID = 55
1053 | 19 | System56 | System ID = 56
1072 | 19 | System57 | System ID = 57
1091 | 19 | System58 | System ID = 58
1110 | 19 | System59 | System ID = 59
1129 | 19 | System60 | System ID = 60
1148 | 1 | IDU Identifier | I = 0x49
1149 | 1 | IDU MODE | 0x30=Fan 0x31=Heat 0x32=Cool 0x33=Dry
1150 | 1 | IDU MODE Mode | 0x30 = Auto,0x31 = Manual
1151 | 2 | Tset | Range: (0-30)d=(0x30,0x30-0x31,0x45)ASCII
1153 | 1 | Tset Mode | 0x30 = Auto,0x31 = Manual
1154 | 1 | Tshift | 0x30 = -5 0x31 = -4 0x32 = -3 0x33 = -2 0x34 = -1 0x35 = 0 0x36 = 1 0x37 = 2 0x38 = 3 0x39 = 4 0x40 = 5
1155 | 1 | Tshift Mode | 0x30 = Auto,0x31 = Manual
1156 | 1 | Fan Speed | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H 0x35 = Free
1157 | 1 | Fan Speed Mode | 0x30 = Auto,0x31 = Manual
1158 | 1 | Status ON/OFF | 0x30 = OFF 0x31 = ON
1159 | 1 | Status ON/OFF Mode | 0x30 = Auto,0x31 = Manual
1160 | 5 | EXV | Decimal Range : -520 to 520 Total 5bytes1 for polarity +’ = Positive ‘-‘ = Negative 'a' = absolute And4 bytes for value Range:(0 to520)d=(0-208)h (0x30x30,0x30,0x30 – 0x32,0x30,0x38)ASCII
1165 | 1 | EXV Mode | 0x30 = Auto,0x31 = Manual
1166 | 1 | IDU Capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw 0x4C = 'L' = 44.0Kw 0x4D = 'M' = 52.7Kw 0x4E = 'N' = 70.3Kw 0x4F = 'O' = 87.9Kw 0x50 = 'P' = 105.5Kw | missing : 0X51='Q'=122.5Kw | No
1167 | 1 | IDU Capacity Mode | 0x30 = Auto,0x31 = Manual
1168 | 1 | Swing | 0x30 =ON, 0x31 = F1, 0x32 = F2, 0x33 = F3, 0x34 = F4, 0x35 = F5 0x36 = FL Reset
1169 | 1 | Swing Mode | 0x30 = Auto,0x31 = Manual
1170 | 1 | IDU on Lock | 0x30 = Unlocked 0x31 = Locked
1171 | 1 | IDU on Lock Mode | 0x30 = Auto,0x31 = Manual
1172 | 1 | IDU off Lock | 0x30 = Unlocked 0x31 = Locked
1173 | 1 | IDU off Lock Mode | 0x30 = Auto,0x31 = Manual
1174 | 1 | IDU Mode Lock | 0x30 = Unlocked 0x31 = Locked
1175 | 1 | IDU Mode Lock Mode | 0x30 = Auto,0x31 = Manual
1176 | 1 | IDU Temp Lock | 0x30 = Unlocked 0x31 = Locked
1177 | 1 | IDU Temp Lock Mode | 0x30 = Auto,0x31 = Manual
1178 | 4 | Start Time | 2Byte for Hour 2Byte for Minute
1182 | 1 | Start Time Mode | 0x30 = Auto,0x31 = Manual
1183 | 4 | End Time | 2Byte for Hour 2Byte for Minute
1187 | 1 | End Time Mode | 0x30 = Auto,0x31 = Manual
1188 | 1 | Sleep Mode | 0x30 = OFF 0x31 = ON
1189 | 1 | Sleep Mode Mode | 0x30 = Auto,0x31 = Manual
1190 | 1 | Future bytes | 'X'
1191 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
1193 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
1197 | 1 | # | End of Data
1198 | Total No of Bytes

## IVRF Configuration Download
|  |  |  | Issues or changes | ODU Firmware change required?
Frame From PC Monitoring to ODU Master for Configuration Download Request
* ¦ P¦ C ¦ Frame Count ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | C | Command Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | B
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 2 | Command | For System Configuration Download 02d=(02)h=(0x30,0x32)ASCII
9 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
11 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
15 | 1 | # | End of Data
16 | Total No of Bytes
Reply From ODU Master to PC Monitoring for Configuration Download
* ¦ M¦ O ¦ XXI¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame From ODU Master to PC Monitoring
2 | 1 | O | Congiguration Data
3 | 3 | XXI | IVRF
6 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
8 |  | ODU Master Configuration
8 | 1 | Master | 0x30
9 | 2 | IDU Quantity | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
11 | 1 | ODU Quantity | (1-3)d=(1-3)h=(0x31-0x33) | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
12 | 1 | ODU Address | (1-3)d=(1-3)h=(0x31-0x33) | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
13 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
14 | 1 | Silent Mode | 0x30= Not Effect 0x31= Always ON 0x32= Select Timer
15 | 1 | Silent Level | 0x30=High 0x31=Low
16 | 1 | Heat/Cool/Free | 0x30=FREE 0x31=HEAT 0x32=COOL
17 | 1 | Comp. Backup | 0x30=Digital 0x31=Fix1 0x32=Fix2 0x33=ODU
18 | 1 | Demand Mode | 0x30= No control 0x31=Always as per level 0x32=As per timer
19 | 1 | Demand Level | 0x30=0 0x31=1 0x32=2 0x33=3
20 | 1 | Test (Performance) | 0x30=0 0x31=1 0x32=2 0x33=3 0x34=4
21 | 2 | Group No. | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
23 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
39 |  | ODU Slave1 Configuration
39 | 1 | Slave1 | 0x31
40 | 2 | IDU Quantity | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
42 | 1 | ODU Quantity | (1-3)d=(1-3)h=(0x31-0x33) | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
43 | 1 | ODU Address | (1-3)d=(1-3)h=(0x31-0x33) | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
44 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
45 | 1 | Silent Mode | 0x30= Not Effect 0x31= Always ON 0x32= Select Timer
46 | 1 | Silent Level | 0x30=High 0x31=Low
47 | 1 | Heat/Cool/Free | 0x30=FREE 0x31=HEAT 0x32=COOL
48 | 1 | Comp. Backup | 0x30=Digital 0x31=Fix1 0x32=Fix2 0x33=ODU
49 | 1 | Demand Mode | 0x30= No control 0x31=Always as per level 0x32=As per timer
50 | 1 | Demand Level | 0x30=0 0x31=1 0x32=2 0x33=3
51 | 1 | Test (Performance) | 0x30=0 0x31=1 0x32=2 0x33=3 0x34=4
52 | 2 | Group No. | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
54 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
70 |  | ODU Slave2 Configuration
70 | 1 | Slave2 | 0x32
71 | 2 | IDU Quantity | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
73 | 1 | ODU Quantity | (1-3)d=(1-3)h=(0x31-0x33) | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
74 | 1 | ODU Address | (1-3)d=(1-3)h=(0x31-0x33) | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
75 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
76 | 1 | Silent Mode | 0x30= Not Effect 0x31= Always ON 0x32= Select Timer
77 | 1 | Silent Level | 0x30=High 0x31=Low
78 | 1 | Heat/Cool/Free | 0x30=FREE 0x31=HEAT 0x32=COOL
79 | 1 | Comp. Backup | 0x30=Digital 0x31=Fix1 0x32=Fix2 0x33=ODU
80 | 1 | Demand Mode | 0x30= No control 0x31=Always as per level 0x32=As per timer
81 | 1 | Demand Level | 0x30=0 0x31=1 0x32=2 0x33=3
82 | 1 | Test (Performance) | 0x30=0 0x31=1 0x32=2 0x33=3 0x34=4
83 | 2 | Group No. | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
85 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
101 |  | IDU Configuration
101 | 2 | IDU1 ID | (01)d=(01)h=(0x30,0x31)ASCII
103 | 1 | IDU Type | 1 - Hiwall 2 - Ducted 3 - 4 way large cst 4 - compact 5 - ceiling concealed 6 - floor mount 7 - TFA 8 - Heat recovery 9 - One way A - 2 way cst
104 | 1 | IDU Capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw 0x4C = 'L' = 44.0Kw 0x4D = 'M' = 52.7Kw 0x4E = 'N' = 70.3Kw 0x4F = 'O' = 87.9Kw 0x50 = 'P' = 105.5Kw | missing : 0X51='Q'=122.5Kw | No
105 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
121 | 20 | IDU2 | IDU ID = 02
141 | 20 | IDU3 | IDU ID = 03
161 | 20 | IDU4 | IDU ID = 04
181 | 20 | IDU5 | IDU ID = 05
201 | 20 | IDU6 | IDU ID = 06
221 | 20 | IDU7 | IDU ID = 07
241 | 20 | IDU8 | IDU ID = 08
261 | 20 | IDU9 | IDU ID = 09
281 | 20 | IDU10 | IDU ID = 10
301 | 20 | IDU11 | IDU ID = 11
321 | 20 | IDU12 | IDU ID = 12
341 | 20 | IDU13 | IDU ID = 13
361 | 20 | IDU14 | IDU ID = 14
381 | 20 | IDU15 | IDU ID = 15
401 | 20 | IDU16 | IDU ID = 16
421 | 20 | IDU17 | IDU ID = 17
441 | 20 | IDU18 | IDU ID = 18
461 | 20 | IDU19 | IDU ID = 19
481 | 20 | IDU20 | IDU ID = 20
501 | 20 | IDU21 | IDU ID = 21
521 | 20 | IDU22 | IDU ID = 22
541 | 20 | IDU23 | IDU ID = 23
561 | 20 | IDU24 | IDU ID = 24
581 | 20 | IDU25 | IDU ID = 25
601 | 20 | IDU26 | IDU ID = 26
621 | 20 | IDU27 | IDU ID = 27
641 | 20 | IDU28 | IDU ID = 28
661 | 20 | IDU29 | IDU ID = 29
681 | 20 | IDU30 | IDU ID = 30
701 | 20 | IDU31 | IDU ID = 31
721 | 20 | IDU32 | IDU ID = 32
741 | 20 | IDU33 | IDU ID = 33
761 | 20 | IDU34 | IDU ID = 34
781 | 20 | IDU35 | IDU ID = 35
801 | 20 | IDU36 | IDU ID = 36
821 | 20 | IDU37 | IDU ID = 37
841 | 20 | IDU38 | IDU ID = 38
861 | 20 | IDU39 | IDU ID = 39
881 | 20 | IDU40 | IDU ID = 40
901 | 20 | IDU41 | IDU ID = 41
921 | 20 | IDU42 | IDU ID = 42
941 | 20 | IDU43 | IDU ID = 43
961 | 20 | IDU44 | IDU ID = 44
981 | 20 | IDU45 | IDU ID = 45
1001 | 20 | IDU46 | IDU ID = 46
1021 | 20 | IDU47 | IDU ID = 47
1041 | 20 | IDU48 | IDU ID = 48
1061 | 20 | IDU49 | IDU ID = 49
1081 | 20 | IDU50 | IDU ID = 50
1101 | 20 | IDU51 | IDU ID = 51
1121 | 20 | IDU52 | IDU ID = 52
1141 | 20 | IDU53 | IDU ID = 53
1161 | 20 | IDU54 | IDU ID = 54
1181 | 20 | IDU55 | IDU ID = 55
1201 | 20 | IDU56 | IDU ID = 56
1221 | 20 | IDU57 | IDU ID = 57
1241 | 20 | IDU58 | IDU ID = 58
1261 | 20 | IDU59 | IDU ID = 59
1281 | 20 | IDU60 | IDU ID = 60
1301 | 20 | IDU61 | IDU ID = 61
1321 | 20 | IDU62 | IDU ID = 62
1341 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
1343 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
1347 | 1 | # | End of Data
1348 | Total No of Bytes

## IVRF Configuration Upload
[5 empty] | Issues or changes | ODU Firmware change required?
From PC Monitoring to ODU Master for Configuration Upload
* ¦ P ¦ D ¦ Frame Count ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | From PC Monitoring to ODU Master
2 | 1 | O | Congiguration Data
3 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 53F
6 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
8 |  | ODU Master Configuration
8 | 1 | Master | 0x30
9 | 2 | IDU Quantity | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
11 | 1 | ODU Quantity | (1-3)d=(1-3)h=(0x31-0x33) |  | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
12 | 1 | ODU Address | (1-3)d=(1-3)h=(0x31-0x33) |  | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
13 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
14 | 1 | Silent Mode | 0x30= Not Effect 0x31= Always ON 0x32= Select Timer
15 | 1 | Silent Level | 0x30=High 0x31=Low
16 | 1 | Heat/Cool/Free | 0x30=FREE 0x31=HEAT 0x32=COOL
17 | 1 | Comp. Backup | 0x30=Digital 0x31=Fix1 0x32=Fix2 0x33=ODU
18 | 1 | Demand Mode | 0x30= No control 0x31=Always as per level 0x32=As per timer
19 | 1 | Demand Level | 0x30=0 0x31=1 0x32=2 0x33=3
20 | 1 | Test (Performance) | 0x30=0 0x31=1 0x32=2 0x33=3 0x34=4
21 | 2 | Group No. | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
23 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
39 |  | ODU Slave1 Configuration
39 | 1 | Slave1 | 0x31
40 | 2 | IDU Quantity | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
42 | 1 | ODU Quantity | (1-3)d=(1-3)h=(0x31-0x33) |  | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
43 | 1 | ODU Address | (1-3)d=(1-3)h=(0x31-0x33) |  | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
44 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP | VRF Capacity Codes 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP 0x46 = 'F' = 4 HP 0x47 = 'G' = 5 HP 0x48 = 'H' = 6 HP
45 | 1 | Silent Mode | 0x30= Not Effect 0x31= Always ON 0x32= Select Timer
46 | 1 | Silent Level | 0x30=High 0x31=Low
47 | 1 | Heat/Cool/Free | 0x30=FREE 0x31=HEAT 0x32=COOL
48 | 1 | Comp. Backup | 0x30=Digital 0x31=Fix1 0x32=Fix2 0x33=ODU
49 | 1 | Demand Mode | 0x30= No control 0x31=Always as per level 0x32=As per timer
50 | 1 | Demand Level | 0x30=0 0x31=1 0x32=2 0x33=3
51 | 1 | Test (Performance) | 0x30=0 0x31=1 0x32=2 0x33=3 0x34=4
52 | 2 | Group No. | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
54 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
70 |  | ODU Slave2 Configuration
70 | 1 | Slave2 | 0x32
71 | 2 | IDU Quantity | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
73 | 1 | ODU Quantity | (1-3)d=(1-3)h=(0x31-0x33) |  | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
74 | 1 | ODU Address | (1-3)d=(1-3)h=(0x31-0x33) |  | (1-4)d = (1-4)h | Yes, if Slave 3 ODU related parameters need to be added
75 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
76 | 1 | Silent Mode | 0x30= Not Effect 0x31= Always ON 0x32= Select Timer
77 | 1 | Silent Level | 0x30=High 0x31=Low
78 | 1 | Heat/Cool/Free | 0x30=FREE 0x31=HEAT 0x32=COOL
79 | 1 | Comp. Backup | 0x30=Digital 0x31=Fix1 0x32=Fix2 0x33=ODU
80 | 1 | Demand Mode | 0x30= No control 0x31=Always as per level 0x32=As per timer
81 | 1 | Demand Level | 0x30=0 0x31=1 0x32=2 0x33=3
82 | 1 | Test (Performance) | 0x30=0 0x31=1 0x32=2 0x33=3 0x34=4
83 | 2 | Group No. | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
85 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
101 |  | IDU Configuration
101 | 2 | IDU1 ID | (01)d=(01)h=(0x30,0x31)ASCII
103 | 1 | IDU Type | 1 - Hiwall 2 - Ducted 3 - 4 way large cst 4 - compact 5 - ceiling concealed 6 - floor mount 7 - TFA 8 - Heat recovery 9 - One way A - 2 way cst
104 | 1 | IDU Capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw 0x4C = 'L' = 44.0Kw 0x4D = 'M' = 52.7Kw 0x4E = 'N' = 70.3Kw 0x4F = 'O' = 87.9Kw 0x50 = 'P' = 105.5Kw |  | missing : 0X51='Q'=122.5Kw | No
105 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
121 | 20 | IDU2 | IDU ID = 02
141 | 20 | IDU3 | IDU ID = 03
161 | 20 | IDU4 | IDU ID = 04
181 | 20 | IDU5 | IDU ID = 05
201 | 20 | IDU6 | IDU ID = 06
221 | 20 | IDU7 | IDU ID = 07
241 | 20 | IDU8 | IDU ID = 08
261 | 20 | IDU9 | IDU ID = 09
281 | 20 | IDU10 | IDU ID = 10
301 | 20 | IDU11 | IDU ID = 11
321 | 20 | IDU12 | IDU ID = 12
341 | 20 | IDU13 | IDU ID = 13
361 | 20 | IDU14 | IDU ID = 14
381 | 20 | IDU15 | IDU ID = 15
401 | 20 | IDU16 | IDU ID = 16
421 | 20 | IDU17 | IDU ID = 17
441 | 20 | IDU18 | IDU ID = 18
461 | 20 | IDU19 | IDU ID = 19
481 | 20 | IDU20 | IDU ID = 20
501 | 20 | IDU21 | IDU ID = 21
521 | 20 | IDU22 | IDU ID = 22
541 | 20 | IDU23 | IDU ID = 23
561 | 20 | IDU24 | IDU ID = 24
581 | 20 | IDU25 | IDU ID = 25
601 | 20 | IDU26 | IDU ID = 26
621 | 20 | IDU27 | IDU ID = 27
641 | 20 | IDU28 | IDU ID = 28
661 | 20 | IDU29 | IDU ID = 29
681 | 20 | IDU30 | IDU ID = 30
701 | 20 | IDU31 | IDU ID = 31
721 | 20 | IDU32 | IDU ID = 32
741 | 20 | IDU33 | IDU ID = 33
761 | 20 | IDU34 | IDU ID = 34
781 | 20 | IDU35 | IDU ID = 35
801 | 20 | IDU36 | IDU ID = 36
821 | 20 | IDU37 | IDU ID = 37
841 | 20 | IDU38 | IDU ID = 38
861 | 20 | IDU39 | IDU ID = 39
881 | 20 | IDU40 | IDU ID = 40
901 | 20 | IDU41 | IDU ID = 41
921 | 20 | IDU42 | IDU ID = 42
941 | 20 | IDU43 | IDU ID = 43
961 | 20 | IDU44 | IDU ID = 44
981 | 20 | IDU45 | IDU ID = 45
1001 | 20 | IDU46 | IDU ID = 46
1021 | 20 | IDU47 | IDU ID = 47
1041 | 20 | IDU48 | IDU ID = 48
1061 | 20 | IDU49 | IDU ID = 49
1081 | 20 | IDU50 | IDU ID = 50
1101 | 20 | IDU51 | IDU ID = 51
1121 | 20 | IDU52 | IDU ID = 52
1141 | 20 | IDU53 | IDU ID = 53
1161 | 20 | IDU54 | IDU ID = 54
1181 | 20 | IDU55 | IDU ID = 55
1201 | 20 | IDU56 | IDU ID = 56
1221 | 20 | IDU57 | IDU ID = 57
1241 | 20 | IDU58 | IDU ID = 58
1261 | 20 | IDU59 | IDU ID = 59
1281 | 20 | IDU60 | IDU ID = 60
1301 | 20 | IDU61 | IDU ID = 61
1321 | 20 | IDU62 | IDU ID = 62
1341 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
1343 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
1347 | 1 | # | End of Data
1348 | Total No of Bytes
ACK or NACK Frame From ODU Master to PC Monitoring
* ¦ M ¦ A ¦ XI ¦ System ID ¦ Frame Count ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Bootloader Frame
2 | 1 | A / N | 'A' = Ack frame 'N' = Nack frame
3 | 2 | XI | IVRF
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | C
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes

## ODUm-ODUs Communication
Frame From ODU Master to Slave for Data
* ¦ M ¦ D ¦ Frame Count ¦ S ¦ Slave ID ¦ Data ¦ Protocol Version ¦ CRC¦ # |  |  |  |  | * ¦ M ¦ D ¦ Frame Count ¦ S ¦ Slave ID ¦ Data ¦ Protocol Version ¦ CRC¦ #
IVRF 6th Gen Parameter Details
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description | Remark | Parameter | Description | Remark
0 | 1 | * | Start of frame |  | * | Start of frame
1 | 1 | M | Frame from ODU Master |  | M | Frame from ODU Master
2 | 1 | D | Slave Data |  | D | Slave Data
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 24 | total number of bytes in a complete frame including start of frame | No. of characters in the Frame before CRC including '*' =in Hex= | 24 | total number of bytes in a complete frame including start of frame
5 | 1 | S | Slave Identifier |  | S | Slave Identifier
6 | 1 | Slave ID | (1-2)d=(0x31-0x32)ASCII |  | Slave ID | (1-2)d=(0x31-0x32)ASCII
7 | 1 | ODU Mode Act | 0x30 = Off 0x31 = Heat 0x32 = Cool |  | ODU Mode Act | 0x30 = Off 0x31 = Heat 0x32 = Cool
8 | 1 | System 3min OFF | 0x30 = OFF 0x31 = On |  | System 3min OFF | 0x30 = OFF 0x31 = On 0x32 = On + Defrost 0x33 = Start Motor Reverse Rotation
9 | 1 | Defrost | 0x30 = Normal operation 0x31 = Go defrost |  | Defrost | 0x30 = Normal Operation 0x31 = Sense Defrost 0x32 = Wait_For_Defrost_Delay 0x33 = Wait_For_Refrigerant_Recovery 0x34 = Start_Defrost 0x35 = Do_Defrost 0x36 = Defrost_Special_Control 0x37 = Complete_Defrost 0x38 = All_Self_Oil_Recovery
10 | 1 | Oil Swap | 0x30 = Normal operation 0x31 = Supplier 0x30 = OFF |  | Oil Swap | 0x30 = Normal operation 0x31 = Supplier 0x30 = OFF
11 | 1 | ODU Startup Flag | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII |  | ODU Startup Flag | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII
12 | 4 | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII |  | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII
16 | 3 | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII |  | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII
19 | 3 | EXV2 Step |  |  | EXV2 Step
22 | 1 | Slave Correspond Control State | Four_Way_Correspond_Control_Start = '1' Referigerant_Recovery_Start = '2' Referigerant_Push_Out_Start = '3' Special_Control_End = '4' HP_Protection_In_Cool_Mode_Start = '5' |  | Slave Correspond Control State | Four_Way_Correspond_Control_Start = '1' Referigerant_Recovery_Start = '2' Referigerant_Push_Out_Start = '3' Special_Control_End = '4' HP_Protection_In_Cool_Mode_Start = '5' During 3 off timer, so no special control ongoing= '0' IDU Oil Pump Out = 'F'
23 | 1 | System Defrost State | System_Defrost_Complete = '0' System_In_Defrost = '1' |  | System Defrost State | System_Defrost_Complete = '0' System_In_Defrost = '1'
24 | 1 | ODU Check Mode | 0x30 = OFF 0x31 = On |  | ODU Check Mode | 0x30 = OFF 0x31 = On
25 | 1 | ODU Commissioning Mode | 0x30 = OFF 0x31 = On |  | ODU Commissioning Mode | 0x30 = OFF 0x31 = On
26 | 1 | Slave Homming | H' = Start Homming |  | Slave Homming | H' = Start Homming
27 | 1 | Gas Shortage in running ODU |  |  | Gas Shortage in running ODU
28 | 1 | Slave Fan Speed |  |  | Slave Fan Speed
29 | 5 | Future Bytes | '0' |  | Future Bytes | Byte 1 - Silent mode Byte 2 - Unload Valve State from Master Byte 3 - Keep 30rps in oil swap Byte 4 - Performance mode case Byte 5 - Compressor type
34 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII |  | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
36 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission |  | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
40 | 1 | # | End of Data |  | # | End of Data
41 | Total No of Bytes
Reply From Slave to ODU Master for Slave Data |  |  |  |  | Reply From Slave to ODU Master for Slave Data
* ¦ S ¦ D ¦ Frame Count ¦ Slave ID ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description |  | Parameter | Description
0 | 1 | * | Start of frame |  | * | Start of frame
1 | 1 | S | Frame From slave |  | S | Frame From slave
2 | 1 | D | Slave data |  | D | Slave data
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | A4 |  | No. of characters in the Frame before CRC including '*' =in Hex= | FFFFFFFFFB
5 | 1 | Slave ID | (1-3)d=(0x31-0x32)ASCII |  | Slave ID | (1-3)d=(0x31-0x32)ASCII
6 | 1 | CAP | VRF ODU Capacity Codes 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP 0x46 = 'F' = 4 HP 0x47 = 'G' = 5 HP 0x48 = 'H' = 6 HP |  | CAP | VRF ODU Capacity Codes 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP 0x46 = 'F' = 4 HP 0x47 = 'G' = 5 HP 0x48 = 'H' = 6 HP
7 | 1 | Liquid Injection Stae | SV4 OFF SV5 OFF SV6 OFF = '0' SV4 ON SV5 OFF SV6 OFF = '1' SV4 ON SV5 ON SV6 OFF = '2' SV4 ON SV5 ON SV6 ON = '3' |  | Liquid Injection Stae | SV4 OFF SV5 OFF SV6 OFF = '0' SV4 ON SV5 OFF SV6 OFF = '1' SV4 ON SV5 ON SV6 OFF = '2' SV4 ON SV5 ON SV6 ON = '3'
8 | 3 | DBG | Debugging Byte |  | DBG | Debugging Byte
11 | 1 | ODU 3 min OFF | 0x30 = OFF 0x31 = ON |  | ODU 3 min OFF | 0x30 = OFF 0x31 = ON
12 | 1 | Inv1 3 min off |  |  | Inv1 3 min off
13 | 1 | Inv2 3 min off |  |  | Inv2 3 min off
14 | 3 | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII |  | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII
17 | 2 | Slave F/w |  |  | Slave F/w
19 | 2 | SPPR F/w |  |  | Fan Drive 1 FW version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
21 | 2 | Fan F/w |  |  | Fan Drive 2 FW version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
23 | 3 | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII |  | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII
26 | 3 | Low pressure |  |  | Low pressure
29 | 3 | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII |  | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII
32 | 3 | Tsat corresponding to Low pressure |  |  | Tsat corresponding to Low pressure
35 | 3 | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII |  | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII
38 | 3 | DLT2 |  |  | DLT2
41 | 3 | Inv1 Current |  |  | Inv1 Current
44 | 3 | Inv2 Current |  |  | Inv2 Current
47 | 3 | Inv1 Temp |  |  | Inv1 Temp
50 | 3 | Inv2 Temp |  |  | Inv2 Temp
53 | 3 | Inv1 DC |  |  | Inv1 DC
56 | 3 | Inv2 DC |  |  | Inv2 DC
59 | 4 | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) |  | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
63 | 4 | Tliq1 |  |  | Tliq1
67 | 4 | Tgas2 |  |  | Tgas2
71 | 4 | Tliq2 |  |  | Tliq2
75 | 4 | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) |  | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
79 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 |  | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34
81 | 2 | Last err |  |  | Last err
83 | 3 | Vr |  |  | Oil Temp1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
86 | 3 | Vy |  |  | Oil Temp2 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
89 | 3 | Vb |  |  | Suction Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
92 | 3 | Set RPS1 |  |  | Set RPS1
95 | 3 | Set RPS2 |  |  | Set RPS2
98 | 3 | F/b RPS1 |  |  | F/b RPS1
101 | 3 | F/b RPS2 |  |  | F/b RPS2
104 | 1 | 4W V | 0x30 = OFF 0x31 = ON |  | 4W V | 0x30 = OFF 0x31 = ON
105 | 1 | SORV |  |  | SORV
106 | 1 | OPOV |  |  | OPOV
107 | 1 | ORCV |  |  | ORCV
108 | 1 | LIBA |  |  | LIBA
109 | 1 | LIA1 |  |  | LIA1
110 | 1 | MLQV |  |  | MLQV
111 | 1 | HGD State |  |  | HGD State
112 | 1 | ULV1 |  |  | ULV1
113 | 1 | ULV2 |  |  | ULV2
114 | 1 | AROLV |  |  | AROLV
115 | 1 | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII |  | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII
116 | 3 | Fan1 speed rpm | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII |  | Fan1 speed rpm | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII
119 | 3 | Fan2 speed rpm |  |  | Fan2 speed rpm
122 | 1 | Fix 1 Startup Flag |  |  | Fix 1 Startup Flag
123 | 1 | Fix 2 Startup Flag |  |  | Fix 2 Startup Flag
124 | 1 | HPS | 0x30 = OFF 0x31 = ON |  | HPS | 0x30 = OFF 0x31 = ON
125 | 1 | LPS |  |  | LPS
126 | 1 | HP_Sw |  |  | HP_Sw
127 | 1 | DLT |  |  | DLT
128 | 1 | PR |  |  | Fan Motor 1 Phase Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
129 | 1 | SP
130 | 1 | Phase_Imbalance
131 | 1 | UV |  |  | Fan Drive 1 IPM Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
132 | 1 | OV
133 | 1 | CP1
134 | 1 | CP2 |  |  | Fan Drive 1 HVDC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
135 | 1 | IT1
136 | 1 | IT2
|  | Pretrip Counts |  |  | Pretrip Counts
137 | 1 | OC1 | (0-15)d = (0-F)h Unsigned Char |  | Fan Motor 2 Phase Current | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
138 | 1 | OC2
139 | 1 | OLL1
140 | 1 | OLL2 |  |  | Fan Drive 2 IPM Temp | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
141 | 1 | OL1
142 | 1 | OL2
143 | 1 | OH1 |  |  | Fan Drive 2 HVDC | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII Unsigned int
144 | 1 | OH2
145 | 1 | SE1
146 | 1 | SE2 |  |  | Unused | Unused
147 | 2 | Slave Time Since Startup | (00-FF)h |  | Slave Time Since Startup
149 | 1 | Backup Mode |  |  | Backup Mode
150 | 1 | DLT Protection Level |  |  | DLT Protection Level | 0x30 = Level 0 0x31 = Level 1 0x32 = Level 2 0x33 = Level 3 0X34 = Level 4
151 | 1 | Comp. 1 Current Protection |  |  | Comp. 1 Current Protection | 0x30 = Level 0 0x31 = Level 1 0x32 = Level 2 0x33 = Level 3
152 | 1 | Comp. 2 Current Protection |  |  | Comp. 2 Current Protection | 0x30 = Level 0 0x31 = Level 1 0x32 = Level 2 0x33 = Level 3
153 | 1 | Inv1 IPM Protection |  |  | Inv1 IPM Protection | 0x30 = Level 0 0x31 = Level 1 0x32 = Level 2 0x33 = Level 3 0X34 = Level 4
154 | 1 | Inv2 IPM Protection |  |  | Inv2 IPM Protection | 0x30 = Level 0 0x31 = Level 1 0x32 = Level 2 0x33 = Level 3 0X34 = Level 4
155 | 1 | Reserved |  |  | Slave1: Comp1 Oil Level | Data to sent in Hex Format 0 to 64H corresponds to 0 to 100% oil percentage
156 | 1 | Reserved |  |  | Slave1: Comp2 Oil Level | Data to sent in Hex Format 0 to 64H corresponds to 0 to 100% oil percentage
157 | 2 | Reserved |  |  | Slave1: Comp Drive 1 FW version | (01-256)d=(01-FF)h Unsigned Char
159 | 2 | Reserved |  |  | Slave1: Comp Drive 2 FW version | (01-256)d=(01-FF)h Unsigned Char
161 | 1 | Reserved |  |  | Slave Ambient Protection State | 0x30 = No Protection 0x31 = Protection is On and restricted at level 1 (85RPS) 0x32 = Protection is on and restricted at level 2 (75RPS)
162 | 2 | Reserved |  |  | Reserved Bytes | Reserved Bytes
164 | 4 | CRC |  |  | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
168 | 1 | # |  |  | # | End of Data
169 | Total No of Bytes

## ODU-IDU Communication
Frame From ODU Master to IDU for IDU Data
* ¦ M¦ D ¦ Frame Count ¦ IDU ID ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description | Remark
0 | 1 | * | Start of frame
1 | 1 | M | Frame from ODU Master
2 | 1 | D | IDU Data
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 1B | total number of bytes in a complete frame including start of frame
5 | 2 | IDU ID | (1-64)d=(0-40)h=(0x30,0x31-0x34,0x30)
7 | 1 | ODU Mode Act | 0x30 = Off 0x31 = Heat 0x32 = Cool
8 | 1 | System 3min OFF | 0x30 = OFF 0x31 = ON
9 | 5 | EXV step of IDU | Decimal Range : -520 to 520 Total 5bytes1 for polarity +’ = Positive ‘-‘ = Negative 'a' = absolute And4 bytes for value Range:(0 to520)d=(0-208)h (0x30x30,0x30,0x30 – 0x32,0x30,0x38)ASCII
14 | 1 | Set Fan Speed by ODU | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H 0x35 = Free
15 | 2 | ODU Error Code | 0xC1-0xC6 0xE1-0xEF 0xF1-0xFF
17 | 2 | Commisioning/Check Mode | Commisioning mode = 'C' & 'M' Check Mode = 'C' & 'K' Hot Gas Defrost ='H' & 'G' else '0' & '0'
19 | 1 | Permit Mode Change | 0' - Reject Mode Change '1' - Accept Mode Change
20 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
22 | 3 | Reserved | "0000"
25 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
27 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
31 | 1 | # | End of Data
32 | Total No of Bytes
Reply From IDU to ODU Master for Data
* ¦ I ¦ D ¦ Frame Count ¦ IDU ID ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | I | Frame From IDU
2 | 1 | D | IDU Data
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 42
5 | 2 | IDU ID | (01 - 62)d=(01- 3E)h=(0x30,0x31 - 0x33,0x45)ASCII
7 | 1 | IDU Type | 1 - Hiwall 2 - Ducted 3 - 4 way large cst 4 - compact 5 - ceiling concealed 6 - floor mount 7 - TFA 8 - Heat recovery 9 - One way A - 2 way cst
8 | 1 | Mode Selected | 0x30 = Off 0x31 = Heat 0x32 = Cool
9 | 1 | IDU status | 0x30 = OFF 0x31 = ON
10 | 1 | IDU capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw
11 | 2 | IDU error code | Range:(U0-UF)=(0x55,0x30-0x55,0x46)ASCII
13 | 3 | DeltaT | 1 byte for polarity ‘+’ = Positive ‘-‘ = Negative 2 bytes for Value Decimal range 0.0 to 5.0 (give dec point frm pc by/10) For communication range is 0 to 50 (0x30,0x30-0x33,0x32)ASCII
16 | 4 | Troom | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
20 | 4 | Tliq | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
24 | 4 | Tgas | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
28 | 4 | Tsupply
32 | 2 | DCL | Range:(0-101)d=(0x30,0x30-0x36,0x35)ASCII
34 | 4 | delta Tcoil | Decimal range: -20.0 to 30.0 °C with resolution of 0.5 Total 4 bytes1 byte for polarity‘ +’ = Positive ‘-‘ = Negative And3 bytes for value Range: 0.0 to 30.0 (0 to 300)d=(0-12C)h (0x30,0x30,0x30 to 0x31,0x32,0x43)ASCII
38 | 2 | user set | Range: (0-30)d=(0x30,0x30-0x31,0x45)ASCII
40 | 1 | Actual Fan Speed | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H 0x35 = Free
41 | 1 | Set Fan Speed By IDU
42 | 1 | flap position | Range: (1-5)d=(1-5)h=(0x31-0x35)ASCII
43 | 1 | pump on/off | 0x30 = OFF 0x31 = ON
44 | 1 | IDU 1 min OFF | 0x30 = OFF 0x31 = ON
45 | 1 | Door Key Status | 0x30 = OFF 0x31 = ON
46 | 2 | IDU Program Version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII
48 | 1 | IDU on Lock | 0x30 = Unlocked 0x31 = Locked
49 | 1 | IDU off Lock | 0x30 = Unlocked 0x31 = Locked
50 | 1 | IDU Mode Lock | 0x30 = Unlocked 0x31 = Locked
51 | 1 | IDU Temp Lock | 0x30 = Unlocked 0x31 = Locked
52 | 4 | Start Time | 2Byte for Hour 2Byte for Minute
56 | 4 | End Time | 2Byte for Hour 2Byte for Minute
60 | 1 | Sleep Mode | 0x30 = OFF 0x31 = ON
61 | 1 | IDU_Drain_Pump_Lock
62 | 1 | IDU_Door_Key_Lock
63 | 1 | IDU Backup Commapd | 'R'=(0x52)ASCII Reset "C4" error of ODU( IDU which is in "C4" error will be kept in backup mode)
64 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
66 | 4 | CRC | 16 bit CRC calculated including * and converted to 4 byte ASCII hex for transmission
70 | 1 | # | End of Data
71 | Total No of Bytes

## IVRF Slave ODU Parameters
Frame From ODU Master to Slave for Slave Parameter upload
* ¦ M¦ V ¦ Frame Count ¦ Slave Status ¦ Data ¦ Protocol Version ¦ CRC¦ #
NOTE: 1. for Slave1 & Slave2, 1) PERF, 2)CHKM , 3)SLTM , 4)SLTL , 5)DMDL parameters are not used. So, keep these parameter text boxes disabled in PC software. And send 0x30 for above parameters in protocol bytes which will be ignored while data processing at Slave ODU. 2. By default, mode selection for every parameter is Auto.
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame from ODU Master
2 | 1 | V | Slave Parameters
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 39
5 | 1 | S | S1 for Slave 1, S2 for Slave 2, S3 for Slave 3
6 | 1 | 1,2 or 3
7 | 3 | Set RPS | to Set 80 RPS for INV 1, Set RPS = 180 to Set 80 RPS for INV 2, Set RPS = 280 to Set 80 RPS for INV 1 and INV2, Set RPS = 380 to Set 80 RPS for INV1 and 0 RPS for INV2, Set RPS = 480
10 | 1 | RPS Mode | 0x30 = Auto,0x31 = Manual
11 | 1 | SV6 | 0x30 = OFF 0x31 = ON
12 | 1 | SV6 Mode | 0x30 = Auto,0x31 = Manual
13 | 1 | SV7 | 0x30 = OFF 0x31 = ON
14 | 1 | SV7 Mode | 0x30 = Auto,0x31 = Manual
15 | 1 | 4W V | 0x30 = OFF 0x31 = ON
16 | 1 | 4W V Mode | 0x30 = Auto,0x31 = Manual
17 | 1 | SORV | 0x30 = OFF 0x31 = ON
18 | 1 | SORV Mode | 0x30 = Auto,0x31 = Manual
19 | 1 | OPOV | 0x30 = OFF 0x31 = ON
20 | 1 | OPOV Mode | 0x30 = Auto,0x31 = Manual
21 | 1 | ORCV | 0x30 = OFF 0x31 = ON
22 | 1 | ORCV Mode | 0x30 = Auto,0x31 = Manual
23 | 1 | LIBA | 0x30 = OFF 0x31 = ON
24 | 1 | LIBA Mode | 0x30 = Auto,0x31 = Manual
25 | 1 | LIA1 | 0x30 = OFF 0x31 = ON
26 | 1 | LIA1 Mode | 0x30 = Auto,0x31 = Manual
27 | 1 | Reserved
28 | 1 | Reserved
29 | 1 | Reserved
30 | 1 | Reserved
31 | 1 | MLQV | 0x30 = OFF 0x31 = ON
32 | 1 | MLQV Mode | 0x30 = Auto,0x31 = Manual
33 | 1 | HOTD | 0x30 = OFF 0x31 = ON
34 | 1 | HOTD Mode | 0x30 = Auto,0x31 = Manual
35 | 1 | Reserved
36 | 1 | Reserved
37 | 1 | Reserved
38 | 1 | Reserved
39 | 1 | Reserved
40 | 1 | Reserved
41 | 1 | Reserved
42 | 1 | Reserved
43 | 1 | Reserved
44 | 1 | Reserved
45 | 1 | Reserved
46 | 1 | CHKM | 0x30 = OFF 0x31 = ON
47 | 1 | CHKM Mode | 0x30 = Auto,0x31 = Manual
48 | 1 | Reserved
49 | 1 | Reserved
50 | 1 | Reserved
51 | 1 | Reserved
52 | 1 | Reserved
53 | 1 | Reserved
54 | 1 | Reserved
55 | 1 | FanSp | Range: (0=11)d=(0-B)h=(0x30,0x42)ASCII
56 | 1 | FanSp Mode | 0x30 = Auto,0x31 = Manual
57 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
61 | 1 | # | End of Data
62 | Total No of Bytes

## Slave Config Download
Frame From ODU Master to Slave for Slave Configuration Download Request
* ¦ M ¦ O ¦ Frame Count ¦ S ¦ Slave ID ¦ Config type ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame from ODU Master
2 | 1 | O | Config frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | D
5 | 1 | S | Slave Identifier
6 | 1 | Slave ID | (1-2)d=(0x31-0x32)ASCII
7 | 1 | 'R' | Config Request
8 | 1 | 'X' | For Future use
9 | 1 | 'X'
10 | 1 | 'X'
11 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
13 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
17 | 1 | # | End of Data
18 | Total No of Bytes
Reply From Slave to ODU Master for Slave Configuration Download
* ¦ S ¦ O ¦ Frame Count ¦ Slave ID ¦ Config type ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | S | Frame From slave
2 | 1 | O | Config farme
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 23
5 | 1 | Slave ID | (1-2)d=(0x31-0x32)ASCII
6 | 1 | 'D' | Config Request
7 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
8 | 1 | Silent Mode | 0x30= Not Effect 0x31= Always ON 0x32= Select Timer
9 | 1 | Silent Level | 0x30=High 0x31=Low
10 | 1 | Heat/Cool/Free | 0x30=FREE 0x31=HEAT 0x32=COOL
11 | 1 | Comp. Backup | 0x30=Digital 0x31=Fix1 0x32=Fix2 0x33=ODU
12 | 1 | Demand Mode | 0x30= No control 0x31=Always as per level 0x32=As per timer
13 | 1 | Demand Level | 0x30=0 0x31=1 0x32=2 0x33=3
14 | 1 | Test (Performance) | 0x30=0 0x31=1 0x32=2 0x33=3 0x34=4
15 | 2 | Group No. | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
17 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
33 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
35 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
39 | 1 | # | End of Data
40 | Total No of Bytes

## Slave Config Upload
Frame From ODU Master to Slave for Slave Configuration Upload
* ¦ M ¦ O ¦ Frame Count ¦ S ¦ Slave ID ¦ Config type ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame from ODU Master
2 | 1 | O | Config frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 24
5 | 1 | S | Slave Identifier
6 | 1 | Slave ID | (1-2)d=(0x31-0x32)ASCII
7 | 1 | 'D' | Config Request
8 | 1 | ODU Capacity | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
9 | 1 | Silent Mode | 0x30= Not Effect 0x31= Always ON 0x32= Select Timer
10 | 1 | Silent Level | 0x30=High 0x31=Low
11 | 1 | Heat/Cool/Free | 0x30=FREE 0x31=HEAT 0x32=COOL
12 | 1 | Comp. Backup | 0x30=Digital 0x31=Fix1 0x32=Fix2 0x33=ODU
13 | 1 | Demand Mode | 0x30= No control 0x31=Always as per level 0x32=As per timer
14 | 1 | Demand Level | 0x30=0 0x31=1 0x32=2 0x33=3
15 | 1 | Test (Performance) | 0x30=0 0x31=1 0x32=2 0x33=3 0x34=4
16 | 2 | Group No. | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
18 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
34 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
36 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
40 | 1 | # | End of Data
41 | Total No of Bytes
Reply From Slave to ODU Master for Slave Configuration Upload
* ¦ S ¦ O ¦ Frame Count ¦ Slave ID ¦ Config type ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | S | Frame From slave
2 | 1 | O | Config farme
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C
5 | 1 | Slave ID | (1-2)d=(0x31-0x32)ASCII
6 | 1 | 'A' | for Config Ack
7 | 1 | 'X' | For Future use
8 | 1 | 'X'
9 | 1 | 'X'
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes

## Set IDU Parameters
Frame From ODU Master to IDU for IDU Parameters Upload
* ¦ M¦ C ¦ Frame Count ¦ Data ¦ IDU Status ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame from ODU Master
2 | 1 | C | IDU Parameters
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 3B
5 | 1 | IDU MODE | 0x30=Fan 0x31=Heat 0x32=Cool 0x33=Dry | 0
6 | 1 | IDU MODE Mode | 0x30 = Auto,0x31 = Manual | 1
7 | 2 | Tset | Range: (0-30)d=(0x30,0x30-0x31,0x45)ASCII | 2
9 | 1 | Tset Mode | 0x30 = Auto,0x31 = Manual | 4
10 | 1 | Tshift | 0x30 = -5 0x31 = -4 0x32 = -3 0x33 = -2 0x34 = -1 0x35 = 0 0x36 = 1 0x37 = 2 0x38 = 3 0x39 = 4 0x40 = 5 | 5
11 | 1 | Tshift Mode | 0x30 = Auto,0x31 = Manual | 6
12 | 1 | Fan Speed | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H 0x35 = Free | 7
13 | 1 | Fan Speed Mode | 0x30 = Auto,0x31 = Manual | 8
14 | 1 | Status ON/OFF | 0x30 = OFF 0x31 = ON | 9
15 | 1 | Status ON/OFF Mode | 0x30 = Auto,0x31 = Manual | 10
16 | 1 | IDU Capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw | 11
17 | 1 | IDU Capacity Mode | 0x30 = Auto,0x31 = Manual | 12
18 | 1 | Swing | 0x30 =ON, 0x31 = F1, 0x32 = F2, 0x33 = F3, 0x34 = F4, 0x35 = F5, 0x36 = Filter RESET | 13
19 | 1 | Swing Mode | 0x30 = Auto,0x31 = Manual | 14
20 | 1 | IDU on Lock | 0x30 = Unlocked 0x31 = Locked | 15
21 | 1 | IDU on Lock Mode | 0x30 = Auto,0x31 = Manual | 16
22 | 1 | IDU off Lock | 0x30 = Unlocked 0x31 = Locked | 17
23 | 1 | IDU off Lock Mode | 0x30 = Auto,0x31 = Manual | 18
24 | 1 | IDU Mode Lock | 0x30 = Unlocked 0x31 = Locked | 19
25 | 1 | IDU Mode Lock Mode | 0x30 = Auto,0x31 = Manual | 20
26 | 1 | IDU Temp Lock | 0x30 = Unlocked 0x31 = Locked | 21
27 | 1 | IDU Temp Lock Mode | 0x30 = Auto,0x31 = Manual | 22
28 | 4 | Start Time | 2Byte for Hour 2Byte for Minute | 23
32 | 1 | Start Time Mode | 0x30 = Auto,0x31 = Manual | 27
33 | 4 | End Time | 2Byte for Hour 2Byte for Minute | 28
37 | 1 | End Time Mode | 0x30 = Auto,0x31 = Manual | 32
38 | 1 | Sleep Mode | 0x30 = OFF 0x31 = ON | 33
39 | 1 | Sleep Mode Mode | 0x30 = Auto,0x31 = Manual | 34
40 | 1 | Future bytes | 'X' | 35
41 | 2 | IDU1 to IDU8 | If Bit=1 then IDU State=Active If Bit=0 then IDU State=Inactive Bit 0-> IDU1 State Bit 1-> IDU2 State Bit 2-> IDU3 State Bit 3-> IDU4 State Bit 4-> IDU5 State Bit 5-> IDU6 State Bit 6-> IDU7 State Bit 7-> IDU8 State e.g. if IDU 1,4,5 & 8 are Active then Byte=0x99 99h=0x39,0x39 (ASCII) D4=0x39 D5=0x39
43 | 2 | IDU9 to IDU16 | Bit 0-> IDU9 State Bit 1-> IDU10 State Bit 2-> IDU11State Bit 3-> IDU12 State Bit 4-> IDU13 State Bit 5-> IDU14 State Bit 6-> IDU15 State Bit 7-> IDU16 State
45 | 2 | IDU17 to IDU24 | Bit 0-> IDU17 State Bit 1-> IDU18 State Bit 2-> IDU19State Bit 3-> IDU20 State Bit 4-> IDU21 State Bit 5-> IDU22 State Bit 6-> IDU23 State Bit 7-> IDU24 State
47 | 2 | IDU25 to IDU32 | Bit 0-> IDU25 State Bit 1-> IDU26 State Bit 2-> IDU27State Bit 3-> IDU28 State Bit 4-> IDU29 State Bit 5-> IDU30 State Bit 6-> IDU31 State Bit 7-> IDU32 State
49 | 2 | IDU33 to IDU40 | Bit 0-> IDU33 State Bit 1-> IDU34 State Bit 2-> IDU35State Bit 3-> IDU36 State Bit 4-> IDU37 State Bit 5-> IDU38 State Bit 6-> IDU39 State Bit 7-> IDU40 State
51 | 2 | IDU41 to IDU48 | Bit 0-> IDU41 State Bit 1-> IDU42 State Bit 2-> IDU43State Bit 3-> IDU44 State Bit 4-> IDU45 State Bit 5-> IDU46 State Bit 6-> IDU47 State Bit 7-> IDU48 State
53 | 2 | IDU49 to IDU56 | Bit 0-> IDU49 State Bit 1-> IDU50 State Bit 2-> IDU51State Bit 3-> IDU52 State Bit 4-> IDU53 State Bit 5-> IDU54 State Bit 6-> IDU55 State Bit 7-> IDU56 State
55 | 2 | IDU57 to IDU64 | Bit 0-> IDU57 State Bit 1-> IDU58 State Bit 2-> IDU59State Bit 3-> IDU60 State Bit 4-> IDU61 State Bit 5-> IDU62 State Bit 6-> IDU63 State Bit 7-> IDU64 State
57 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
59 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
63 | 1 | # | End of Data
64 | Total No of Bytes

## IDU Config Download
Frame From ODU Master to IDU for Configuration Download Request
* ¦ M¦ O ¦ Frame Count ¦IDU ID ¦ Config Type ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame | *MO0E01IRXXX034D31#
1 | 1 | M | Frame from ODU Master
2 | 1 | O | Config Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | E
5 | 2 | IDU ID | (01 - 62)d=(01- 3E)h=(0x30,0x31 - 0x33,0x45)ASCII
7 | 1 | 'I' | IDU Identifier for IDU Configuration
8 | 1 | 'R' | Config request
9 | 1 | 'X' | For Future use
10 | 1 | 'X'
11 | 1 | 'X'
12 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
14 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
18 | 1 | # | End of Data
19 | Total No of Bytes
Reply From IDU to ODU Master for Configuration Download
* ¦ I ¦ O ¦ Frame Count ¦ IDU ID ¦ Config Type ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame | *IO1E01D4202$$$$$$$$$$$$$$$$0BFB6A#
1 | 1 | I | Frame From IDU
2 | 1 | O | Config Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 1E
5 | 2 | IDU ID | (01 - 62)d=(01- 3E)h=(0x30,0x31 - 0x33,0x45)ASCII
7 | 1 | 'D' | for Config Data
8 | 1 | IDU Type | 1 - Hiwall 2 - Ducted 3 - 4 way large cst 4 - compact 5 - ceiling concealed 6 - floor mount 7 - TFA 8 - Heat recovery 9 - One way A - 2 way cst
9 | 1 | IDU Capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw
10 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
12 | 16 | IDU Label | 16 Alfanumeric Characters
28 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
30 | 4 | CRC | 16 bit CRC calculated including * and converted to 4 byte ASCII hex for transmission
34 | 1 | # | End of Data
35 | Total No of Bytes

## IDU Config Upload
Frame From ODU Master to IDU for Configuration Upload
* ¦ M¦ O ¦ Frame Count ¦IDU ID ¦ Config Type ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame from ODU Master
2 | 1 | O | Config Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 1F
5 | 2 | IDU ID | (01 - 62)d=(01- 3E)h=(0x30,0x31 - 0x33,0x45)ASCII
7 | 1 | 'I' | IDU Identifier for IDU Configuration
8 | 1 | 'D' | Config data
9 | 1 | IDU Type | 1 - Hiwall 2 - Ducted 3 - 4 way large cst 4 - compact 5 - ceiling concealed 6 - floor mount 7 - TFA 8 - Heat recovery 9 - One way A - 2 way cst
10 | 1 | IDU Capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw
11 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
13 | 16 | IDU Label | 16 Alfanumeric Characters
29 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
31 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
35 | 1 | # | End of Data
36 | Total No of Bytes
Reply From IDU to ODU Master for Configuration Upload
* ¦ I ¦ O ¦ Frame Count ¦ IDU ID ¦ Config Type ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | I | Frame From IDU
2 | 1 | O | Congiguration Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | D
5 | 2 | IDU ID | (01 - 62)d=(01- 3E)h=(0x30,0x31 - 0x33,0x45)ASCII
7 | 1 | 'A' | for Config Ack
8 | 1 | 'X' | For Future use
9 | 1 | 'X'
10 | 1 | 'X'
11 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
13 | 4 | CRC | 16 bit CRC calculated including * and converted to 4 byte ASCII hex for transmission
17 | 1 | # | End of Data
18 | Total No of Bytes

## Auto Addressing
Frame From ODU Master to IDU for Start of Autoadressing
* ¦ M ¦ B/T ¦ Frame Count ¦ 64¦ Command ¦ No of IDUs ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description |  | no of IDU
0 | 1 | * | Start of frame | *MB0C64101039B05# | 1
1 | 1 | M | Frame from master | *MB0C64102039BF5# | 2
2 | 1 | B or T | B = Broadcast frame T = Restart Auto addressing | *MB0C64103035BA4# | 3
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C | *MB0C64104039A15# | 4
5 | 2 | 64
7 | 1 | Command | 1 = Start of auto adress
8 | 2 | No of IDUs connected | 1 to 62
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes
Frame From ODU Master to IDU for Who is IDU 'X'
* ¦ M ¦ B ¦ Frame Count ¦ IDU ID¦ Command ¦ XX ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description |  | no of IDU
0 | 1 | * | Start of frame | *MB0C012XX03B2EB# | 1
1 | 1 | M | Frame from master | *MB0C022XX0381EB# | 2
2 | 1 | B | Broadcast frame | *MB0C032XX0350EA# | 3
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C | *MB0C042XX03E7EB# | 4
5 | 2 | IDU ID | 1 to 62
7 | 1 | Command | 2 = Who is 'X'
8 | 2 | Future bytes | XX
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes
Reply Frame From IDU to ODU Master for Who is IDU 'X'
* ¦ I ¦ U ¦ Frame Count ¦ IDU ID¦ Random no ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description |  | no of IDU
0 | 1 | * | Start of frame | *IU0C016BD0BF7B9# | 1
1 | 1 | I | Frame from IDU | *IU0C026BD0BC4B9# | 2
2 | 1 | U | Reply of who is X | *IU0C036BD0B15B8# | 3
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C | *IU0C046BD0BA2B9# | 4
5 | 2 | IDU ID | 1 to 62
7 | 3 | Random no | 000 to FFF
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes
Frame From ODU Master to IDU for Recalculation
* ¦ M ¦ B ¦ Frame Count ¦ IDU ID¦ Command ¦ X ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description |  | no of IDU
0 | 1 | * | Start of frame | *MB0C0131X03EECB# | 1
1 | 1 | M | Frame from master | *MB0C0231X03DDCB# | 2
2 | 1 | B | Broadcast frame | *MB0C0331X030CCA# | 3
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C | *MB0C0431X03BBCB# | 4
5 | 2 | Recalculate ID from this No to no of IDU ID | 1 to 62
7 | 2 | Command | 31 = Recalculate
9 | 1 | Future bytes | X
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes
Frame From ODU Master to IDU for IDU ID Confirmation
* ¦ M ¦ U ¦ Frame Count ¦ IDU ID¦ Command ¦ X ¦ Random No ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description |  | no of IDU
0 | 1 | * | Start of frame | *MU0F0132XXXX0379AC# | 1
1 | 1 | M | Frame from master | *MU0F0232XXXX0389B8# | 2
2 | 1 | U | Confirmation frame | *MU0F0332XXXX0319B5# | 3
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | F | *MU0F0432XXXX032993# | 4
5 | 2 | Confirm IDU ID | 1 to 62 | *MU0F0332X33703FE93#
7 | 2 | Command | 32 = IDU ID Confrmation
9 | 1 | Future bytes | X | *MU0F0432XF9B03072A#
10 | 3 | Random No Received from IDU in reply of who is 'X' | 000 to FFF
13 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
15 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
19 | 1 | # | End of Data
20 | Total No of Bytes
Reply Frame From IDU to ODU Master for IDU ID Confirmation
* ¦ I ¦ A ¦ Frame Count ¦ IDU ID¦ 32X ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description |  | no of IDU
0 | 1 | * | Start of frame | *IA0C0132X0BB1EE# | 1
1 | 1 | I | Frame from IDU | *IA0C0232X0B82EE# | 2
2 | 1 | A | Ack frame | *IA0C0332X0B53EF# | 3
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C | *IA0C0432X0BE4EE# | 4
5 | 2 | IDU ID | 1 to 62
7 | 3 |  | 32X
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes
Frame From ODU Master to IDU for End of Autoadressing
* ¦ M ¦ B ¦ Frame Count ¦ 65 ¦ Command ¦ XX ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame | *MB0C654XX033604#
1 | 1 | M | Frame from master
2 | 1 | B | B = Broadcast frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C
5 | 2 | 65
7 | 1 | Command | 4 = Endt of auto adress
8 | 2 | Future bytes | XX
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes
no of IDU
|  |  | *MD1B0120a01E050000X02XXX035292# |  | 1
|  |  | *MD1B0220a01E050000X02XXX0361A1# |  | 2
|  |  | *MD1B0320a01E050000X02XXX03B0B1# |  | 3
|  |  | *MD1B0420a01E050000X02XXX0307C7# |  | 4

## Start of BL Session
Frame From PC Monitoring to ODU Master for Start of Bootloader Session Command
* ¦ B ¦ Dest Type ¦ Dest ID ¦ System ID ¦ Frame Count ¦ Command ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | B | Bootloader Frame
2 | 1 | Destination Type | 1 - Hiwall 2 - Ducted 3 - 4 way large cst 4 - compact 5 - ceiling concealed 6 - floor mount 7 - TFA 8 - Heat recovery 9 - One way A - 2 way cst
3 | 2 | Destination ID | 00d = 00h = For All Types (01-62)d = (01-3E)h = For IDU ID 63d = 3Fh = For Slave 1 64d = 40h = For Slave 2
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | F
10 | 1 | C | Command Frame
11 | 2 | Command | 01d = 01h = Start of BL Session
13 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
15 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
19 | 1 | # | End of Data
20 | Total No of Bytes
Frame From ODU Master to Slave or IDU for Start of Bootloader Session Command
* ¦ B ¦ Dest Type ¦ Dest ID ¦ System ID ¦ Frame Count ¦ Command ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | B | Bootloader Frame
2 | 1 | Destination Type | '1' = 0x31 = HiWall 2TR '2' = 0x32 = Ducted '3' = 0x33 = 4Way '4' = 0x34 = Mini 4Way '5' = 0x35 = Ceiling Concealed '6' = 0x36 = Floor '7' = 0x37 = TFA '8' = 0x38 = Heat Recovery '9' = 0x39 = HiWall 1.5TR 'A' = 0x41 = Master 'B' = 0x42 = Slave
3 | 2 | Destination ID | 00d = 00h = For All Types (01-62)d = (01-3E)h = For IDU ID 63d = 3Fh = For Slave 1 64d = 40h = For Slave 2
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | F
10 | 1 | C | Command Frame
11 | 2 | Command | 01d = 01h = Start of BL Session
13 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
15 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
19 | 1 | # | End of Data
20 | Total No of Bytes
ACK or NACK Frame From ODU Master to PC Monitoring
* ¦ M ¦ A ¦ XX ¦ System ID ¦ Frame Count ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Bootloader Frame
2 | 1 | A / N | 'A' = Ack frame 'N' = Nack frame
3 | 2 | XX | Extra Bytes
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | C
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes

## Block Programming
Frame From PC Monitoring to ODU Master for Block Programming
* ¦ B ¦ Dest Type ¦ Dest ID ¦ System ID ¦ Frame Count ¦ Command ¦ Addr ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | B | Bootloader Frame
2 | 1 | Destination Type | 1 - Hiwall 2 - Ducted 3 - 4 way large cst 4 - compact 5 - ceiling concealed 6 - floor mount 7 - TFA 8 - Heat recovery 9 - One way A - 2 way cst
3 | 2 | Destination ID | 00d = 00h = For All Types (01-62)d = (01-3E)h = For IDU ID 63d = 3Fh = For Slave 1 64d = 40h = For Slave 2
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 215
10 | 1 | C | Command Frame
11 | 2 | Command | 02d = 02h = Block Programming Frame
13 | 6 | Block Address | 3 Byte Flash Address
19 | 512 | Block Data | 256 Bytes Flash Data
531 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
533 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
537 | 1 | # | End of Data
538 | Total No of Bytes
Frame From ODU Master to Slave or IDU for Block Programming
* ¦ B ¦ Dest Type ¦ Dest ID ¦ System ID ¦ Frame Count ¦ Command ¦ Addr ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | B | Bootloader Frame
2 | 1 | Destination Type | '1' = 0x31 = HiWall 2TR '2' = 0x32 = Ducted '3' = 0x33 = 4Way '4' = 0x34 = Mini 4Way '5' = 0x35 = Ceiling Concealed '6' = 0x36 = Floor '7' = 0x37 = TFA '8' = 0x38 = Heat Recovery '9' = 0x39 = HiWall 1.5TR 'A' = 0x41 = Master 'B' = 0x42 = Slave
3 | 2 | Destination ID | 00d = 00h = For All Types (01-62)d = (01-3E)h = For IDU ID 63d = 3Fh = For Slave 1 64d = 40h = For Slave 2
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 215
10 | 1 | C | Command Frame
11 | 2 | Command | 02d = 02h = Block Programming Frame
13 | 6 | Block Address | 3 Byte Flash Address
19 | 512 | Block Data | 256 Bytes Flash Data
531 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
533 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
537 | 1 | # | End of Data
538 | Total No of Bytes
ACK or NACK Frame From ODU Master to PC Monitoring
* ¦ M ¦ A ¦ XX ¦ System ID ¦ Frame Count ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Bootloader Frame
2 | 1 | A / N | 'A' = Ack frame 'N' = Nack frame
3 | 2 | XX | Extra Bytes
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | C
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes

## BL Status Polling
Frame From PC Monitoring to ODU Master for Status Polling
* ¦ B ¦ Dest Type ¦ Dest ID ¦ System ID ¦ Frame Count ¦ Command ¦ Addr ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | B | Bootloader Frame
2 | 1 | Destination Type | '1' = 0x31 = HiWall 2TR '2' = 0x32 = Ducted '3' = 0x33 = 4Way '4' = 0x34 = Mini 4Way '5' = 0x35 = Ceiling Concealed '6' = 0x36 = Floor '7' = 0x37 = TFA '8' = 0x38 = Heat Recovery '9' = 0x39 = HiWall 1.5TR 'A' = 0x41 = Master 'B' = 0x42 = Slave
3 | 2 | Destination ID | (01-62)d = (01-3E)h = For IDU ID 63d = 3Fh = For Slave 1 64d = 40h = For Slave 2
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | F
10 | 1 | C | Command Frame
11 | 2 | Command | 03d = 03h = Code Enquiry Frame
13 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
15 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
19 | 1 | # | End of Data
20 | Total No of Bytes
Reply Frame From ODU Master to PC Monitoring for Programming Status of master
* ¦ B ¦ Dest Type ¦ Dest ID ¦ System ID ¦ Frame Count ¦ Programming Status ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | B | Bootloader Frame
2 | 1 | Destination Type | 'P'
3 | 2 | Destination ID | (00)d=(00)h=(0x30,0x30)ASCII
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | E
10 | 1 | R | Reply Frame
11 | 1 | Programming Status | '0' = 0x30 = Failed '1' = 0x31 = Successful 'X' = 0x58 = Not Connected
12 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
14 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
18 | 1 | # | End of Data
19 | Total No of Bytes
Reply Frame From ODU Master to PC Monitoring for Programming Status of IDUs and Slave
* ¦ B ¦ Dest Type ¦ Dest ID ¦ System ID ¦ Frame Count ¦ Programming Status ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | B | Bootloader Frame
2 | 1 | Destination Type | 'A' = 0x41 = Master
3 | 2 | Destination ID | (00)d=(00)h=(0x30,0x30)ASCII
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 4D
10 | 1 | R | Reply Frame
11 | 64 | Programming Status | '0'= 0x30 = Failed '1' = 0x31 = Successful 'X' = 0x58 = Not Connected 65 Bytes for status of 65 devices Byte1 = Status of IDU1 Byte62 = Status of IDU62 Byte63 = Status of Slave1 Byte64 = Status of Slave2
75 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
77 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
81 | 1 | # | End of Data
82 | Total No of Bytes
Frame From ODU Master to Slave or IDU for Status Polling
* ¦ B ¦ Dest Type ¦ Dest ID ¦ System ID ¦ Frame Count ¦ Command ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | B | Bootloader Frame
2 | 1 | Destination Type | 1 - Hiwall 2 - Ducted 3 - 4 way large cst 4 - compact 5 - ceiling concealed 6 - floor mount 7 - TFA 8 - Heat recovery 9 - One way A - 2 way cst
3 | 2 | Destination ID | 00d = 00h = For All Types (01-62)d = (01-3E)h = For IDU ID 63d = 3Fh = For Slave 1 64d = 40h = For Slave 2
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | F
10 | 1 | C | Command Frame
11 | 2 | Command | 03d = 03h = Code Enquiry Frame
13 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
15 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
19 | 1 | # | End of Data
20 | Total No of Bytes
Reply Frame From Slave or IDU to ODU Master for Programming Status
* ¦ B ¦ Dest Type ¦ Dest ID ¦ System ID ¦ Frame Count ¦ Programming Status ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | B | Bootloader Frame
2 | 1 | Destination Type | 'A' = 0x41 = Master
3 | 2 | Destination ID | (00)d=(00)h=(0x30,0x30)ASCII
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | E
10 | 1 | R | Reply Frame
11 | 1 | Programming Status | '0' = 0x30 = Failed '1' = 0x31 = Successful 'X' = 0x58 = Not Connected
12 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
14 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
18 | 1 | # | End of Data
19 | Total No of Bytes

## End of BL Session
Frame From PC Monitoring to ODU Master for End of Bootloader Session Command
* ¦ B ¦ Dest Type ¦ Dest ID ¦ System ID ¦ Frame Count ¦ Command ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | B | Bootloader Frame
2 | 1 | Destination Type | '1' = 0x31 = HiWall 2TR '2' = 0x32 = Ducted '3' = 0x33 = 4Way '4' = 0x34 = Mini 4Way '5' = 0x35 = Ceiling Concealed '6' = 0x36 = Floor '7' = 0x37 = TFA '8' = 0x38 = Heat Recovery '9' = 0x39 = HiWall 1.5TR 'A' = 0x41 = Master 'B' = 0x42 = Slave
3 | 2 | Destination ID | 00d = 00h = For All Types (01-62)d = (01-3E)h = For IDU ID 63d = 3Fh = For Slave 1 64d = 40h = For Slave 2
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | F
10 | 1 | C | Command Frame
11 | 2 | Command | 04d = 04h =End of BL Session
13 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
15 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
19 | 1 | # | End of Data
20 | Total No of Bytes
Frame From ODU Master to Slave or IDU for Start of Bootloader Session Command
* ¦ B ¦ Dest Type ¦ Dest ID ¦ System ID ¦ Frame Count ¦ Command ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | B | Bootloader Frame
2 | 1 | Destination Type | 1 - Hiwall 2 - Ducted 3 - 4 way large cst 4 - compact 5 - ceiling concealed 6 - floor mount 7 - TFA 8 - Heat recovery 9 - One way A - 2 way cst
3 | 2 | Destination ID | 00d = 00h = For All Types (01-62)d = (01-3E)h = For IDU ID 63d = 3Fh = For Slave 1 64d = 40h = For Slave 2
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | F
10 | 1 | C | Command Frame
11 | 2 | Command | 04d = 04h =End of BL Session
13 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
15 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
19 | 1 | # | End of Data
20 | Total No of Bytes
ACK or NACK Frame From ODU Master to PC Monitoring
* ¦ M ¦ A ¦ XX ¦ System ID ¦ Frame Count ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Bootloader Frame
2 | 1 | A / N | 'A' = Ack frame 'N' = Nack frame
3 | 2 | XX | Extra Bytes
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | C
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes

## DC, Moddbus, DA Config
Frame From PC Application to Data Concentrator or Data Acq module or Modbus Converter for no of systems connected
* ¦ D ¦ C ¦ Frame Count ¦ No of systems ¦ XXX ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description | e.g.
0 | 1 | * | Start of frame | *DC0C01XXX0BC64C#
1 | 1 | D |  | *DC0C02XXX0BF54C#
2 | 1 | C/S | C = No of System Configuration E = Energy Meter Quantity Configure S = Slave ID Configuration | *DC0C03XXX0B244D#
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C | *DC0C04XXX0B934C#
5 | 2 | No of Systems & Energy Meter Quantity or Slave ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII or (01 - 247)d=(01- F7)h=(0x30,0x31 - 0x46,0x37)ASCII | *DC0C05XXX0B424D#
7 | 3 | XXX | future bytes | *DC0C06XXX0B714D#
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII | *DC0C07XXX0BA04C#
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission | *DC0C08XXX0B5F4C#
16 | 1 | # | End of Data | *DC0C09XXX0B8E4D#
17 | Total No of Bytes |  |  | *DC0C0AXXX0BF647#
*DC0C0BXXX0BC547#
*DC0C0CXXX0B1446#
*DC0C0DXXX0BA347#
*DC0C0EXXX0B7246#
*DC0C0FXXX0B4146#
*DC0C10XXX0BD75D#
Frame From Data Concentrator or Data Acq module or Modbus Converter to PC Application for acknowledgment
* ¦ D ¦ A ¦ Frame Count ¦ XXX ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | D | data acq frame
2 | 1 | A/N | Ack frame
3 | 4 | No. of characters in the Frame before CRC including '*' =in Hex= | C
7 | 3 | XXX | future byte
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes

## Date Time Config in DA
*DR000E01XXX0A3575#
Request Frame From PC Application to Data Acq module for Date and time
* ¦ D ¦ R ¦ Frame Count ¦ 01 ¦XXX ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | D | data acq frame
2 | 1 | R | Request frame
3 | 4 | No. of characters in the Frame before CRC including '*' =in Hex= | E
7 | 2 | Date time request = 01 | 01d = 0x30,0x31h
9 | 3 | XXX | future byte
12 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
14 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
18 | 1 | # | End of Data
19 | Total No of Bytes
Frame From PC Application to Data Acq module or vice versa for Date and time
* ¦ D ¦ T ¦ Frame Count ¦ DD ¦ M ¦ YYY ¦ HH ¦ MM ¦ SS ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | D | data acq frame
2 | 1 | T | Date time frame
3 | 4 | No. of characters in the Frame before CRC including '*' =in Hex= | 15
7 | 2 | Date | 1 to 31d = 0x30,0x31 to 0x31,0x46h (01-1F)
9 | 1 | Month | 1 to 12d = 0x31 to 0x43h (1-C)
10 | 3 | Year | 1 to 4096d = 0x30,0x30,0x31 to 0x46,0x46,0x46h (001-FFF)
13 | 2 | Hours | 0 to 23d = 0x30,0x30 to 0x31,0x37h (00-17)
15 | 2 | Minute | 0 to 59d = 0x30,0x30 to 0x33,0x42h (00-3B)
17 | 2 | Seconds | 0 to 59d = 0x30,0x30 to 0x33,0x42h (00-3B)
19 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
21 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
25 | 1 | # | End of Data
26 | Total No of Bytes
Frame From Data Acq module to PC Application for acknowledgment
* ¦ D ¦ A ¦ Frame Count ¦ XXX ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | D | data acq frame
2 | 1 | A/N | Ack frame
3 | 4 | No. of characters in the Frame before CRC including '*' =in Hex= | C
7 | 3 | XXX | future byte
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes

## Data Acq Communication
*DR000E02XXX0A0675#
Request Frame From PC Application to Data Acq module for Data
* ¦ D ¦ R ¦ Frame Count ¦ 02 ¦ XXX ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame | *DR000F02A7DC0A3C17#
1 | 1 | D | data acq frame | *DR000F0297DC0A441D#
2 | 1 | R | Request frame
3 | 4 | No. of characters in the Frame before CRC including '*' =in Hex= | F
7 | 2 | Data request = 02 | 02d = 0x30,0x32h
9 | 1 | Month of file to be read | 1 to 12d = 0x31 to 0x43h (1-C)
10 | 3 | Year of file to be read | 1 to 4096d = 0x30,0x30,0x31 to 0x46,0x46,0x46h (001-FFF)
13 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
15 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
19 | 1 | # | End of Data
20 | Total No of Bytes
Reply Frame From Data Acq module to PC for Data
* ¦ D ¦ D ¦ Frame Count ¦ DATA ¦ Protocol Version ¦ CRC ¦ #
Number of systems connected |  | 16
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | D | data acq frame
2 | 1 | D | Data
3 | 4 | No. of characters in the Frame before CRC including '*' =in Hex= | C5C | no of systems = (frame count-28)/196
7 | 2 | Date | 1 to 31d = 0x30,0x31 to 0x31,0x46h (01-1F) | 16
9 | 1 | Month | 1 to 12d = 0x31 to 0x43h (1-C)
10 | 3 | Year | 1 to 4096d = 0x30,0x30,0x31 to 0x46,0x46,0x46h (001-FFF)
13 | 2 | Hours | 0 to 23d = 0x30,0x30 to 0x31,0x37h (00-17)
15 | 2 | Minute | 0 to 59d = 0x30,0x30 to 0x33,0x42h (00-3B)
17 | 2 | Seconds | 0 to 59d = 0x30,0x30 to 0x33,0x42h (00-3B)
19 | 1 | IDU data identifier | I' = 0x49
20 | 992 | IDU Fan Speed | 62 IDU of each 16 Systems Sequentially 1 Byte for 1 IDU so total 992 IDUs 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H
1012 | 992 | IDU DCL | 62 IDU of each 16 Systems Sequentially 1 Byte for 1 IDU so total 992 IDUs 0x30 = DCL is Zero 0x31 = DCl is present
2004 | 992 | IDU Delata T Range | 62 IDU of each 16 Systems Sequentially 1 Byte for 1 IDU so total 992 IDUs 0x31 = if(T<= 2) 0x32 = if(2< T< 10) 0x33 = if(T>= 10)
2996 | 1 | ODU data identifier | O' = 0x4F
2997 | 16 | ODU TOC | 1 Bytes for one system 0x30 = TOC is Zero 0x31 = TOC is present
3013 | 16 | ODU Mode | 1 Bytes for one system 0x30 = Off 0x31 = Heat 0x32 = Cool
3029 | 128 | ODU current Wattage | 8 Bytes for one system not defined yet according to wattmeter specs
3157 | 5 | future bytes | X'
3162 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
3164 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
3168 | 1 | # | End of Data
3169 | Total No of Bytes
Reply Frame From Data Acq module to PC for Data
* ¦ D ¦ D ¦ Frame Count ¦ EOF ¦ Protocol Version ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | D | data acq frame
2 | 1 | D | Data
3 | 4 | No. of characters in the Frame before CRC including '*' =in Hex= | C
7 | 1 | End of file reached | E
8 | 1 |  | O
9 | 1 |  | F
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes

## IVRF Error Logging
ODU Error Log Request by PCM
* ¦ E¦ L ¦ Frame Count ¦ System ID ¦ ODU / IDU ¦ Data Frame No ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | E | Frame from PC Monitoring to ODU Master
2 | 1 | L | Command Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 9
5 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
7 | 1 | ODU or IDU log request | 0x30 - ODU 0x31 - IDU
8 | 1 | Data Frame No | (0-9)d = (0-9)h =(0x30 to 0x39) ASCII
9 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
13 | 1 | # | End of Data
14 | Total No of Bytes
ODU Error Log Upload by ODU Master
* ¦ E ¦ L ¦ Frame Length ¦ System ID ¦ ODU / IDU ¦ Data Frame No ¦ Data(10 Records) ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | E | Frame from PC Monitoring to ODU Master
2 | 1 | L | Command Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 383
5 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
7 | 1 | ODU or IDU log upload | 0x30 - ODU
8 | 1 | Data Frame No | (0-9)d = (0-9)h =(0x30 to 0x39) ASCII
9 |  | Data - Record 1
9 | 6 | DDMMYY
15 | 4 | HHMM
19 | 1 | ODU Type
20 | 2 | Error Code
22 | 4 | General_TOC
26 | 1 | General_LIQinj
27 | 1 | DBG
28 | 3 | General_ECC
31 | 3 | Output_PWM
34 | 1 | Output_FIX1
35 | 1 | Output_FIX2
36 | 1 | Output_WV_4
37 | 1 | Output_HOTD
38 | 3 | Output_EXV1
41 | 3 | Output_EXV2
44 | 3 | Output_Fan1Speed
47 | 3 | Output_Fan2Speed
50 | 3 | Input_HPr
53 | 3 | Input_LPr
56 | 2 | Input_CurrD
58 | 2 | Input_CurrF1
60 | 2 | Input_CurrF2
62 | 3 | Input_DLT1
65 | 3 | Input_DLT2
68 | 3 | Input_DLT3
71 | 4 | Input_Tgas1
75 | 4 | Input_Tgas2
79 | 4 | Input_Tliq1
83 | 4 | Input_Tliq2
87 | 4 | Input_Tamb
91 | 3 | Input_Volt
94 | 1 | Priorities_FIX1
95 | 1 | Priorities_FIX2
96 | 1 | Priorities_StartUpFlag
97 | 1 | Reserved. Used by logging firmware |  | 89
98 | 89 | Data - Record 2
187 | 89 | Data - Record 3
276 | 89 | Data - Record 4
365 | 89 | Data - Record 5
454 | 89 | Data - Record 6
543 | 89 | Data - Record 7
632 | 89 | Data - Record 8
721 | 89 | Data - Record 9
810 | 89 | Data - Record 10
899 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
903 | 1 | # | End of Data
904 | Total No of Bytes
IDU Error Log Upload by ODU Master
* ¦ E ¦ L ¦ Frame Length ¦ System ID ¦ ODU / IDU ¦ Data Frame No ¦ Data(10 Records) ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | E | Frame from PC Monitoring to ODU Master
2 | 1 | L | Command Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 167
5 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
7 | 1 | ODU or IDU log upload | 0x31 - IDU
8 | 1 | Data Frame No | (0-9)d = (0-9)h =(0x30 to 0x39) ASCII
9 |  | Data - Record 1
9 | 6 | DDMMYY
15 | 4 | HHMM
19 | 2 | IDU No
21 | 2 | Error Code
23 | 4 | Tliq
27 | 4 | Tgas
31 | 4 | EXV
35 | 1 | Drain Pump status
36 | 1 | Actual Fan Speed
37 | 4 | Troom
41 | 2 | DCL
43 | 1 | Reserved. Used by logging firmware |  | 35
44 | 35 | Data - Record 2
79 | 35 | Data - Record 3
114 | 35 | Data - Record 4
149 | 35 | Data - Record 5
184 | 35 | Data - Record 6
219 | 35 | Data - Record 7
254 | 35 | Data - Record 8
289 | 35 | Data - Record 9
324 | 35 | Data - Record 10
359 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
363 | 1 | # | End of Data
364 | Total No of Bytes

## ODU Config
Command Frame From Debugger to ODU for ODU Configuration and Auto Address
@Note: 1) This frame needs to be used for ODU Capacity, ODU Mode, Number of IDUs, Number of ODUs, Machine Type and auto-addressing setting through the configuration page. 2) The frame needs ot be updated to send the Slave 1, Slave 2 and Slave 3 related parameters 3) Also need to add a frame between ODUM(Master) and ODUS(Slave) which sends the Slave parameters to the respective Slave ODUs. 4) Whenever this frame is updated and the ODUM-ODUS frame is also added, there will be a change in ODU firmware.
* ¦ O ¦ C ¦ System Type ¦ Configuration Data ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | O
2 | 1 | C
3 | 1 | System Type | "D" - DVRF "I" - IVRF "F" - Freematch
4 |  | Configuration Data
4 | 1 | ODU Capacity Auto / Manual | Auto = '0' Manual = '1'
5 | 1 | ODU Capacity | IVRF - HP_0_Code = '0' HP_7_Code = '1' HP_8_Code = '2' HP_10_Code = '3' HP_12_Code = '4' HP_14_Code = '5' HP_16_Code = '6' HP_18_Code = '7' HP_20_Code = '8' HP_22_Code = '9' DVRF - HP_0_Code = '0' HP_12_Code = '1' HP_14_Code = '2' HP_16_Code = '3' HP_18_Code = '4' HP_21_Code = '5' HP_24_Code = '6' HP_6_Code = '7' HP_7_Code = '8' Freematch - HP_0_Code = '0' HP_3_Code = '1' HP_4_Code = '2' HP_5_Code = '3' HP_6_Code = '4' HP_8_Code = '5' | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM IVRF 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
6 | 1 | ODU Machine Type Auto / Manual | Auto = '0' Manual = '1'
7 | 1 | ODU Machine Type | SC = '0' HP = '1'
8 | 1 | ODU Set Mode Auto / Manual | Auto = '0' Manual = '1'
9 | 1 | ODU Set Mode | Free = '0' Heat = '1' Cool = '2'
10 | 1 | System ID Auto / Manual | Auto = '0' Manual = '1'
11 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
13 | 1 | No of IDUs Auto / Manual | Auto = '0' Manual = '1'
14 | 2 | No fo Idus | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII
16 | 1 | No of ODUs Auto / Manual | Auto = '0' Manual = '1'
17 | 1 | No of ODUs | Range (0-4)d=(0-4)h=(0x30 -0x34)ASCII
18 | 1 | Set Auto Address Flag Auto / Manual | Auto = '0' Manual = '1'
19 | 1 | Set Auto Address Flag | Reset = '0' Set = '1'
20 | 1 | Start Auto Address Auto / Manual | Auto = '0' Manual = '1'
21 | 1 | Set Date Time Auto / Manual | Auto = '0' Manual = '1'
22 | 12 | Set Date Time | DDMMYYYYHHMN
34 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
38 | 1 | # | End of Data
Reply Send from ODU Master
* ¦ O ¦ C ¦ Y / N ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | O
2 | 1 | C
#REF! | 1 | Y or N | "Y" - Ack "N" - Nack
#REF! | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission Unsigned int
#REF! | 1 | # | End of Data
#REF! | Total No of Bytes

## DVRF Slave ODU Parameters
Frame From ODU Master to Slave for Slave Parameter upload
* ¦ M¦ V ¦ Frame Count ¦ Slave Status ¦ Data ¦ Protocol Version ¦ CRC¦ #
NOTE: 1. for Slave1 & Slave2, 1) PERF, 2)CHKM , 3)SLTM , 4)SLTL , 5)DMDL parameters are not used. So, keep these parameter text boxes disabled in PC software. And send 0x30 for above parameters in protocol bytes which will be ignored while data processing at Slave ODU. 2. By default, mode selection for every parameter is Auto.
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame from ODU Master
2 | 1 | V | Slave Parameters
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | 4B
5 | 1 | Slave 1 status | if Byte = '1' slave is active else Byte = '0' slave is Inactive
6 | 1 | Slave 2 status
7 | 3 | PWM | Range:(0-1000)d=(0-3E8)h Remove one dec point frm pc i.e. /10 since range changed from 1000 to 100 (0x30,0x30,0x30 – 0x33,0x45,0x38)ASCII
10 | 1 | PWM Mode | 0x30 = Auto,0x31 = Manual
11 | 1 | Fix1Comp | 0x30 = OFF 0x31 = ON
12 | 1 | Fix1Comp Mode | 0x30 = Auto,0x31 = Manual
13 | 1 | Fix2Comp | 0x30 = OFF 0x31 = ON
14 | 1 | Fix2Comp Mode | 0x30 = Auto,0x31 = Manual
15 | 1 | 4W V | 0x30 = OFF 0x31 = ON
16 | 1 | 4W V Mode | 0x30 = Auto,0x31 = Manual
17 | 1 | SORV | 0x30 = OFF 0x31 = ON
18 | 1 | SORV Mode | 0x30 = Auto,0x31 = Manual
19 | 1 | OPOV | 0x30 = OFF 0x31 = ON
20 | 1 | OPOV Mode | 0x30 = Auto,0x31 = Manual
21 | 1 | ORCV | 0x30 = OFF 0x31 = ON
22 | 1 | ORCV Mode | 0x30 = Auto,0x31 = Manual
23 | 1 | LIBA | 0x30 = OFF 0x31 = ON
24 | 1 | LIBA Mode | 0x30 = Auto,0x31 = Manual
25 | 1 | LIA1 | 0x30 = OFF 0x31 = ON
26 | 1 | LIA1 Mode | 0x30 = Auto,0x31 = Manual
27 | 1 | LIA2 | 0x30 = OFF 0x31 = ON
28 | 1 | LIA2 Mode | 0x30 = Auto,0x31 = Manual
29 | 1 | EVIV | 0x30 = OFF 0x31 = ON display/disable this parameter on software screen
30 | 1 | EVIV Mode | 0x30 = Auto,0x31 = Manual display/disable this parameter on software screen
31 | 1 | MLQV | 0x30 = OFF 0x31 = ON
32 | 1 | MLQV Mode | 0x30 = Auto,0x31 = Manual
33 | 1 | HOTD | 0x30 = OFF 0x31 = ON
34 | 1 | HOTD Mode | 0x30 = Auto,0x31 = Manual
35 | 3 | EXV | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII
38 | 1 | EXV Mode
39 | 2 | IDUqty | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII
41 | 1 | IDUqty Mode | 0x30 = Auto,0x31 = Manual
42 | 1 | PERF | 0x30 = OFF 0x31 = ON
43 | 1 | PERF Mode | 0x30 = Auto,0x31 = Manual
44 | 1 | CHKM | 0x30 = OFF 0x31 = ON
45 | 1 | CHKM Mode | 0x30 = Auto,0x31 = Manual
46 | 1 | SLTM | 0x30 = OFF 0x31 = ON
47 | 1 | SLTM Mode | 0x30 = Auto,0x31 = Manual
48 | 1 | SLTL | 0x30 = OFF 0x31 = ON
49 | 1 | SLTL Mode | 0x30 = Auto,0x31 = Manual
50 | 1 | DMDL | 0x30 = OFF 0x31 = ON
51 | 1 | DMDL Mode | 0x30 = Auto,0x31 = Manual
52 | 1 | MODE | 0x30 = setFREE 0x31 = setHEAT 0x32 = setCOOL
53 | 1 | ODU MODE Mode | 0x30 = Auto,0x31 = Manual
54 | 2 | FanSp | Range: (0=11)d=(0-B)h=(0x30,0x42)ASCII
56 | 1 | FanSp Mode | 0x30 = Auto,0x31 = Manual
57 | 8 | Set Date | Byte1 = D Byte2 = D Byte3 = M Byte4 = M Byte5 = Y Byte6 = Y Byte7 = Y Byte8 = Y
65 | 1 | Set Date Mode | 0x30 = Auto,0x31 = Manual
66 | 6 | Set Time | Byte1 = H Byte2 = H Byte3 = M Byte4 = M Byte5 = S Byte6 = S
72 | 1 | Set Time Mode | 0x30 = Auto,0x31 = Manual
73 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
75 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
79 | 1 | # | End of Data
80 | Total No of Bytes

## DVRF User Frame
Command Frame From PC Monitoring to ODU Master of System for User Data
* ¦ P¦ C ¦ Frame Count ¦ Syatem ID ¦ Command ¦ Data Type(U) ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | C | Command Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C
5 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
7 | 2 | Command | For System Status Data 01d=(01)h=(0x30,0x31)ASCII
9 | 1 | Data Type | For User data 'U' = 0x55
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17
Reply Send from ODU Master of System to PC Monitoring for User Data
* ¦ M¦ D ¦ Frame Count ¦ System Data ¦ Syatem ID¦ Data Type(U) ¦ Protocol Version no ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame From Master to PC monitoring
2 | 1 | D | Data Frame
3 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 706
6 |  | Master Inputs
6 | 1 | ODU Capacity | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw) | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
7 | 4 | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
11 |  | Slave 1 Inputs
11 | 1 | ODU Capacity | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw) | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
12 | 4 | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
16 |  | Slave 2 Inputs
16 | 1 | ODU Capacity | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw) | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
17 | 4 | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
21 |  | Master Output
21 | 1 | Fix1 | 0x30 = OFF 0x31 = ON
22 | 1 | Fix2
23 |  | Slave 1 Output
23 | 1 | Fix1 | 0x30 = OFF 0x31 = ON
24 | 1 | Fix2
25 |  | Slave 2 Output
25 | 1 | Fix1 | 0x30 = OFF 0x31 = ON
26 | 1 | Fix2
27 |  | System Info
27 | 2 | IDUqty | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII
29 | 3 | SUMkw ODU | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII
32 | 4 | SUMkw IDU | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII
36 | 3 | Diversity | Range:(0-150)d=(provision for 0-999)d= (0x30,0x30,0x30-0x33,0x45,0x37)ASCII
39 | 1 | ODU Mode | 0x30 = Off 0x31 = Heat 0x32 = Cool 0x33 = Free
40 |  | General Info Master
40 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34
42 | 2 | Last err
44 |  | General Info Slave 1
44 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34
46 | 2 | Last err
48 |  | General Info Slave 2
48 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34
50 | 2 | Last err
52 | 5 | ODU Future bytes | 'X'
57 |  | IDU1
57 | 1 | IDU mode | 0x30=Fan 0x31=Heat 0x32=Cool 0x33=Dry | 0
58 | 1 | IDU status | 0x30 = OFF 0x31 = ON | 1
59 | 2 | IDU error code | Range:(U0-UF)=(0x55,0x30-0x55,0x46)ASCII | 2
61 | 4 | Troom | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) | 4
65 | 1 | IDU capacity | 0x31 = 2.8KW 0x32 = 3.5KW 0x33 = 4.6KW 0x34 = 5.3KW 0x35 = 7.0KW 0x36 = 7.7KW 0x37 = 8.8KW 0x38 = 10.6KW 0x39 = 12.3KW 0x40 = 14.1KW 0x41 = 17.6KW 0x42 = 19.3KW 0x43 = 21.1KW 0x44 = 23.9KW 0x45 = 28.1KW 0x46 = 35.2KW | 8
66 | 1 | Model name | 0x31 = HiWall 2TR 0x32 = Ducted 0x33 = 4Way 0x34 = Mini 4Way 0x35 = Ceiling Concealed 0x36 = Floor 0x37 = TFA 0x38 = Heat Recovery 0x39 = HiWall 1.5TR | 9
67 | 1 | Set Fan Speed | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H 0x35 = Free | 10
68 | 2 | user set | Range: (0-30)d=(0x30,0x30-0x31,0x45)ASCII | 11
70 | 1 | flap position | 0x30 = Swing ON 0x31 = F1 0x32 = F2 0x33 = F3 0x34 = F4 0x35 = F5 | 13
71 | 1 | IDU on Lock | 0x30 = Unlocked 0x31 = Locked | 14
72 | 1 | IDU off Lock | 0x30 = Unlocked 0x31 = Locked | 15
73 | 1 | IDU Mode Lock | 0x30 = Unlocked 0x31 = Locked | 16
74 | 1 | IDU Temp Lock | 0x30 = Unlocked 0x31 = Locked | 17
75 | 4 | Start Time | 2Byte for Hour 2Byte for Minute | 18
79 | 4 | End Time | 2Byte for Hour 2Byte for Minute | 22
83 | 1 | Sleep Mode | 0x30 = OFF 0x31 = ON | 26
84 | 1 | IDU Future bytes | 'X' | 27
85
85 | 28 | IDU2 | All 28 Bytes are same as IDU1
113 | 28 | IDU3
141 | 28 | IDU4
169 | 28 | IDU5
197 | 28 | IDU6
225 | 28 | IDU7
253 | 28 | IDU8
281 | 28 | IDU9
309 | 28 | IDU10
337 | 28 | IDU11
365 | 28 | IDU12
393 | 28 | IDU13
421 | 28 | IDU14
449 | 28 | IDU15
477 | 28 | IDU16
505 | 28 | IDU17
533 | 28 | IDU18
561 | 28 | IDU19
589 | 28 | IDU20
617 | 28 | IDU21
645 | 28 | IDU22
673 | 28 | IDU23
701 | 28 | IDU24
729 | 28 | IDU25
757 | 28 | IDU26
785 | 28 | IDU27
813 | 28 | IDU28
841 | 28 | IDU29
869 | 28 | IDU30
897 | 28 | IDU31
925 | 28 | IDU32
953 | 28 | IDU33
981 | 28 | IDU34
1009 | 28 | IDU35
1037 | 28 | IDU36
1065 | 28 | IDU37
1093 | 28 | IDU38
1121 | 28 | IDU39
1149 | 28 | IDU40
1177 | 28 | IDU41
1205 | 28 | IDU42
1233 | 28 | IDU43
1261 | 28 | IDU44
1289 | 28 | IDU45
1317 | 28 | IDU46
1345 | 28 | IDU47
1373 | 28 | IDU48
1401 | 28 | IDU49
1429 | 28 | IDU50
1457 | 28 | IDU51
1485 | 28 | IDU52
1513 | 28 | IDU53
1541 | 28 | IDU54
1569 | 28 | IDU55
1597 | 28 | IDU56
1625 | 28 | IDU57
1653 | 28 | IDU58
1681 | 28 | IDU59
1709 | 28 | IDU60
1737 | 28 | IDU61
1765 | 28 | IDU62
1793 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
1795 | 1 | Data Type = U | For Engineering data 'E' = 0x45 For User data 'U' = 0x55
1796 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
1798 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
1802 | 1 | # | End of Data
1803 | Total No of Bytes

## DVRF Engineering Frame
Command Frame From PC Monitoring to ODU Master of System for Engineering Data
* ¦ P¦ C ¦ Frame Count ¦ Syatem ID ¦ Command¦ Data Type(E) ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | C | Command Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C
5 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
7 | 2 | Command | For System Status Data 01d=(01)h=(0x30,0x31)ASCII
9 | 1 | Data Type | For Engineering data 'E' = 0x45
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17
Reply Send from ODU Master of System to PC Monitoring for User data
* ¦ M¦ D ¦ Frame Count ¦ System Data ¦ Syatem ID¦ Data Type(E) ¦ Protocol Version no ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame From Master to PC monitoring
2 | 1 | D | Data Frame
3 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 10FA
6 |  | Master Inputs
6 | 1 | ODU Capacity | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw) | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
7 | 3 | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII
10 | 3 | Low pressure
13 | 3 | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII
16 | 3 | Tsat corresponding to Low pressure
19 | 2 | Digi current | Range: (0-220)d=(0-DC)h give dec point frm pc by/10 (0x30,0x30 – 0x44,0x43)ASCII
21 | 2 | Fix1 current
23 | 2 | Fix2 current
25 | 3 | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII
28 | 3 | DLT2
31 | 3 | DLT3
34 | 4 | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
38 | 4 | Tliq1
42 | 4 | Tgas2
46 | 4 | Tliq2
50 | 4 | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
54 | 3 | supply voltage | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII
Slave 1 Inputs
57 | 1 | ODU Capacity | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw) | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
58 | 3 | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII
61 | 3 | Low pressure
64 | 3 | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII
67 | 3 | Tsat corresponding to Low pressure
70 | 2 | Digi current | Range: (0-220)d=(0-DC)h give dec point frm pc by/10 (0x30,0x30 – 0x44,0x43)ASCII
72 | 2 | Fix1 current
74 | 2 | Fix2 current
76 | 3 | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII
79 | 3 | DLT2
82 | 3 | DLT3
85 | 4 | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
89 | 4 | Tliq1
93 | 4 | Tgas2
97 | 4 | Tliq2
101 | 4 | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
105 | 3 | supply voltage | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII
Slave 2 Inputs
108 | 1 | ODU Capacity | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw) | 0x30 = '0' = 0 0x31 = '1' = 12 HP(35.2kw) 0x32 = '2' = 14 HP(40.8kw) 0x33 = '3' = 16 HP(46.9kw) 0x34 = '4' = 18 HP(52.8kw) 0x35 = '5' = 21 HP(61.2kw) 0x36 = '6' = 24 HP(70.4kw) 0x37 = '7' = 6 HP 0x38 = '8' = 7HP Unsigned Char For SIAM 0x30 = '0' = 0 HP 0x31 = '1' = 7 HP 0x32 = '2' = 8 HP 0x33 = '3' = 10 HP 0x34 = '4' = 12 HP 0x35 = '5' = 14 HP 0x36 = '6' = 16 HP 0x37 = '7' = 18 HP 0x38 = '8' = 20 HP 0x39 = '9' = 22 HP 0x43 = 'C' = 24 HP 0x44 = 'D' = 26 HP 0x45 = 'E' = 28 HP
109 | 3 | High pressure | Range: (0 – 700)d=(0-2BC)h (0x30,0x30,0x30 – 0x32,0x42,0x43)ASCII
112 | 3 | Low pressure
115 | 3 | Tsat corresponding to High pressure | Range: (0 – 512)d=(0-200)h (0x30,0x30,0x30 – 0x32,0x30,0x30)ASCII
118 | 3 | Tsat corresponding to Low pressure
121 | 2 | Digi current | Range: (0-220)d=(0-DC)h give dec point frm pc by/10 (0x30,0x30 – 0x44,0x43)ASCII
123 | 2 | Fix1 current
125 | 2 | Fix2 current
127 | 3 | DLT1 | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII
130 | 3 | DLT2
133 | 3 | DLT3
136 | 4 | Tgas1 | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
140 | 4 | Tliq1
144 | 4 | Tgas2
148 | 4 | Tliq2
152 | 4 | Tamb | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38)
156 | 3 | supply voltage | Range: (000-999)d=(0-3E7)h (0x30,0x30,0x30 – 0x33,0x45,0x37)ASCII
Master Output
159 | 3 | PWM | Decimal Range :(0-1000)d=(0-3E8)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x33,0x45,0x38)ASCII
162 | 1 | Fix1 | 0x30 = OFF 0x31 = ON
163 | 1 | Fix2
164 | 1 | 4W V
165 | 1 | SORV
166 | 1 | OPOV
167 | 1 | ORCV
168 | 1 | LIBA
169 | 1 | LIA1
170 | 1 | LIA2
171 | 1 | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII
172 | 1 | MLQV | 0x30 = OFF 0x31 = ON
173 | 1 | HOTD
174 | 3 | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII
177 | 3 | EXV2 Step
180 | 3 | Fan1 speed rpm | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII
183 | 3 | Fan2 speed rpm
Slave 1 Output
186 | 3 | PWM | Decimal Range :(0-1000)d=(0-3E8)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x33,0x45,0x38)ASCII
189 | 1 | Fix1 | 0x30 = OFF 0x31 = ON
190 | 1 | Fix2
191 | 1 | 4W V
192 | 1 | SORV
193 | 1 | OPOV
194 | 1 | ORCV
195 | 1 | LIBA
196 | 1 | LIA1
197 | 1 | LIA2
198 | 1 | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII
199 | 1 | MLQV | 0x30 = OFF 0x31 = ON
200 | 1 | HOTD
201 | 3 | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII
204 | 3 | EXV2 Step
207 | 3 | Fan1 speed rpm | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII
210 | 3 | Fan2 speed rpm
Slave 2 Output
213 | 3 | PWM | Decimal Range :(0-1000)d=(0-3E8)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x33,0x45,0x38)ASCII
216 | 1 | Fix1 | 0x30 = OFF 0x31 = ON
217 | 1 | Fix2
218 | 1 | 4W V
219 | 1 | SORV
220 | 1 | OPOV
221 | 1 | ORCV
222 | 1 | LIBA
223 | 1 | LIA1
224 | 1 | LIA2
225 | 1 | Fan Step | (0-11)d=(0-B)h (0x30-0x42)ASCII
226 | 1 | MLQV | 0x30 = OFF 0x31 = ON
227 | 1 | HOTD
228 | 3 | EXV1 Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII
231 | 3 | EXV2 Step
234 | 3 | Fan1 speed rpm | Range: (0-1500)d=(0-5DC)h (0x30,0x30,0x30-0x35,0x44,0x43)ASCII
237 | 3 | Fan2 speed rpm
System Info
240 | 2 | IDUqty | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII
242 | 3 | SUMkw ODU | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII
245 | 4 | SUMkw IDU | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII
249 | 3 | Diversity | Range:(0-150)d=(provision for 0-999)d= (0x30,0x30,0x30-0x33,0x45,0x37)ASCII
252 | 4 | SUMkw IDU Thermo ON | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII
256 | 2 | DCLmax | Range:(0-101)d=(0x30,0x30-0x36,0x35)ASCII
258 | 4 | TMC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII
262 | 4 | TSCnew | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII
266 | 4 | TSCold | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII
270 | 4 | BTCnew | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII
274 | 4 | BTCold | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII
278 | 1 | ODU Mode | 0x30 = Free 0x31 = Heat 0x32 = Cool
279 | 1 | Defrost | 0x30 = Normal 0x31 = Go defrost
280 | 1 | ODU Mode Act | 0x30 = Off 0x31 = Heat 0x32 = Cool
General Info Master
281 | 1 | CAP | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw)
282 | 4 | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII
286 | 1 | Defrost | 0x30 = Normal 0x31 = Go defrost
287 | 1 | Self oil recovery | 0x30 = Normal 0x31 = Do Self oil recovery 0x32 = 0x33 =
288 | 1 | Oil Swap | 0x30 = Normal 0x31 = 0x32 = Supplier 0x33 = Receiver
289 | 1 | Liquid inject | 0x30 = OFF 0x31 = ON
290 | 3 | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII | EVI
293 | 1 | System 3min OFF | 0x30 = OFF 0x31 = ON
294 | 1 | ODU 3 min OFF
295 | 1 | Fix1 3 min off
296 | 1 | Fix2 3 min off
297 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34
299 | 2 | Last err
301 | 4 | CAPnew | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw)
305 | 4 | CAPold
309 | 3 | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII
General Info Slave 1
312 | 1 | CAP | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw)
313 | 4 | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII
317 | 1 | Defrost | 0x30 = Normal 0x31 = Go defrost
318 | 1 | Self oil recovery | 0x30 = Normal 0x31 = Do Self oil recovery 0x32 = 0x33 =
319 | 1 | Oil Swap | 0x30 = Normal 0x31 = 0x32 = Supplier 0x33 = Receiver
320 | 1 | Liquid inject | 0x30 = OFF 0x31 = ON
321 | 3 | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII
324 | 1 | System 3min OFF | 0x30 = OFF 0x31 = ON
325 | 1 | ODU 3 min OFF
326 | 1 | Fix1 3 min off
327 | 1 | Fix2 3 min off
328 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34
330 | 2 | Last err
332 | 4 | CAPnew | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw)
336 | 4 | CAPold
340 | 3 | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII
General Info Slave 2
343 | 1 | CAP | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw)
344 | 4 | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII
348 | 1 | Defrost | 0x30 = Normal 0x31 = Go defrost
349 | 1 | Self oil recovery | 0x30 = Normal 0x31 = Do Self oil recovery 0x32 = 0x33 =
350 | 1 | Oil Swap | 0x30 = Normal 0x31 = 0x32 = Supplier 0x33 = Receiver
351 | 1 | Liquid inject | 0x30 = OFF 0x31 = ON
352 | 3 | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII
355 | 1 | System 3min OFF | 0x30 = OFF 0x31 = ON
356 | 1 | ODU 3 min OFF
357 | 1 | Fix1 3 min off
358 | 1 | Fix2 3 min off
359 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34
361 | 2 | Last err
363 | 4 | CAPnew | 0x30 = 0 0x31 = 12 HP(35.2kw) 0x32 = 14 HP(40.8kw) 0x33 = 16 HP(46.9kw) 0x34 = 18 HP(52.8kw) 0x35 = 21 HP(61.2kw) 0x36 = 24 HP(70.4kw)
367 | 4 | CAPold
371 | 3 | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII
Protection Master
374 | 1 | HPS | 0x30 = OFF 0x31 = ON
375 | 1 | LPS
376 | 1 | HP_Sw
377 | 1 | Tc
378 | 1 | Te
379 | 1 | DLT
380 | 1 | PR
381 | 1 | SP
382 | 1 | Phase_Imbalance
383 | 1 | UV
384 | 1 | OV
385 | 1 | OC
Protection Slave 1
386 | 1 | HPS | 0x30 = OFF 0x31 = ON
387 | 1 | LPS
388 | 1 | HP_Sw
389 | 1 | Tc
390 | 1 | Te
391 | 1 | DLT
392 | 1 | PR
393 | 1 | SP
394 | 1 | Phase_Imbalance
395 | 1 | UV
396 | 1 | OV
397 | 1 | OC
Protection Slave 2
398 | 1 | HPS | 0x30 = OFF 0x31 = ON
399 | 1 | LPS
400 | 1 | HP_Sw
401 | 1 | Tc
402 | 1 | Te
403 | 1 | DLT
404 | 1 | PR
405 | 1 | SP
406 | 1 | Phase_Imbalance
407 | 1 | UV
408 | 1 | OV
409 | 1 | OC
Priorities Master
410 | 1 | Fix 1 Startup Flag | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII
411 | 1 | Fix 2 Startup Flag
412 | 1 | ODU Startup Flag
Priorities Slave 1
413 | 1 | Fix 1 Startup Flag | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII
414 | 1 | Fix 2 Startup Flag
415 | 1 | ODU Startup Flag
Priorities Slave 2
416 | 1 | Fix 1 Startup Flag | Range: (0-9)d=(0-9)h =(0x30-0x39)ASCII
417 | 1 | Fix 2 Startup Flag
418 | 1 | ODU Startup Flag
Switch
419 | 1 | performance mode on/off | 0x30 = OFF 0x31 = ON
420 | 1 | check mode
421 | 1 | silent mode
422 | 1 | Silent Level
423 | 1 | Demand Level
424 | 2 | Master Program Version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII
426 | 2 | Slave 1 Program Version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII
428 | 2 | Slave 2 Program Version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII
430 | 5 | ODU Future bytes | 'X'
435 |  | IDU1
435 | 1 | IDU mode | 0x30=Fan 0x31=Heat 0x32=Cool 0x33=Dry | 0
436 | 1 | IDU status | 0x30 = OFF 0x31 = ON | 1
437 | 2 | IDU error code | Range:(U0-UF)=(0x55,0x30-0x55,0x46)ASCII | 2
439 | 2 | DCL | Range:(0-101)d=(0x30,0x30-0x36,0x35)ASCII | 4
441 | 3 | DeltaT | 1 byte for polarity ‘+’ = Positive ‘-‘ = Negative 2 bytes for Value Decimal range 0.0 to 5.0 (give dec point frm pc by/10) For communication range is 0 to 50 (0x30,0x30-0x33,0x32)ASCII | 6
444 | 4 | Troom | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) | 9
448 | 4 | Tliq | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) | 13
452 | 1 | IDU capacity | 0x31 = 2.8KW 0x32 = 3.5KW 0x33 = 4.6KW 0x34 = 5.3KW 0x35 = 7.0KW 0x36 = 7.7KW 0x37 = 8.8KW 0x38 = 10.6KW 0x39 = 12.3KW 0x40 = 14.1KW 0x41 = 17.6KW 0x42 = 19.3KW 0x43 = 21.1KW 0x44 = 23.9KW 0x45 = 28.1KW 0x46 = 35.2KW | 17
453 | 1 | Model name | 0x31 = HiWall 2TR 0x32 = Ducted 0x33 = 4Way 0x34 = Mini 4Way 0x35 = Ceiling Concealed 0x36 = Floor 0x37 = TFA 0x38 = Heat Recovery 0x39 = HiWall 1.5TR | 18
454 | 4 | Tsupply | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) | 19
458 | 4 | Tgas |  | 23
462 | 1 | Thermostat on/off | 0x30 = OFF 0x31 = ON | 27
463 | 1 | Set Fan Speed by ODU | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H 0x35 = Free | 28
464 | 1 | Actual Fan Speed |  | 29
465 | 2 | user set | Range: (0-30)d=(0x30,0x30-0x31,0x45)ASCII | 30
467 | 1 | pump on/off | 0x30 = OFF 0x31 = ON | 32
468 | 1 | flap position | Range: (1-5)d=(1-5)h=(0x31-0x35)ASCII | 33
469 | 1 | swing on/off | 0x30 = OFF 0x31 = ON | 34
470 | 5 | EXV step of IDU | Decimal Range : -520 to 520 Total 5bytes1 for polarity +’ = Positive ‘-‘ = Negative 'a' = absolute And4 bytes for value Range:(0 to520)d=(0-208)h (0x30x30,0x30,0x30 – 0x32,0x30,0x38)ASCII | 35
475 | 4 | delta Tcoil | Decimal range: -20.0 to 30.0 °C with resolution of 0.5 Total 4 bytes1 byte for polarity‘ +’ = Positive ‘-‘ = Negative And3 bytes for value Range: 0.0 to 30.0 (0 to 300)d=(0-12C)h (0x30,0x30,0x30 to 0x31,0x32,0x43)ASCII | 40
479 | 1 | Set Fan Speed By IDU | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H 0x35 = Free | 44
480 | 1 | IDU 1 min OFF |  | 45
481 | 1 | Door Key Status | 0x30 = OFF 0x31 = ON | 46
482 | 2 | IDU Program Version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII | 47
484 | 1 | IDU on Lock | 0x30 = Unlocked 0x31 = Locked | 49
485 | 1 | IDU off Lock | 0x30 = Unlocked 0x31 = Locked | 50
486 | 1 | IDU Mode Lock | 0x30 = Unlocked 0x31 = Locked | 51
487 | 1 | IDU Temp Lock | 0x30 = Unlocked 0x31 = Locked | 52
488 | 4 | Start Time | 2Byte for Hour 2Byte for Minute | 53
492 | 4 | End Time | 2Byte for Hour 2Byte for Minute | 57
496 | 1 | Sleep Mode | 0x30 = OFF 0x31 = ON | 61
497 | 1 | IDU Future bytes | 'X' | 62
498
498 | 63 | IDU2 | All 63 Bytes are same as IDU1
561 | 63 | IDU3
624 | 63 | IDU4
687 | 63 | IDU5
750 | 63 | IDU6
813 | 63 | IDU7
876 | 63 | IDU8
939 | 63 | IDU9
1002 | 63 | IDU10
1065 | 63 | IDU11
1128 | 63 | IDU12
1191 | 63 | IDU13
1254 | 63 | IDU14
1317 | 63 | IDU15
1380 | 63 | IDU16
1443 | 63 | IDU17
1506 | 63 | IDU18
1569 | 63 | IDU19
1632 | 63 | IDU20
1695 | 63 | IDU21
1758 | 63 | IDU22
1821 | 63 | IDU23
1884 | 63 | IDU24
1947 | 63 | IDU25
2010 | 63 | IDU26
2073 | 63 | IDU27
2136 | 63 | IDU28
2199 | 63 | IDU29
2262 | 63 | IDU30
2325 | 63 | IDU31
2388 | 63 | IDU32
2451 | 63 | IDU33
2514 | 63 | IDU34
2577 | 63 | IDU35
2640 | 63 | IDU36
2703 | 63 | IDU37
2766 | 63 | IDU38
2829 | 63 | IDU39
2892 | 63 | IDU40
2955 | 63 | IDU41
3018 | 63 | IDU42
3081 | 63 | IDU43
3144 | 63 | IDU44
3207 | 63 | IDU45
3270 | 63 | IDU46
3333 | 63 | IDU47
3396 | 63 | IDU48
3459 | 63 | IDU49
3522 | 63 | IDU50
3585 | 63 | IDU51
3648 | 63 | IDU52
3711 | 63 | IDU53
3774 | 63 | IDU54
3837 | 63 | IDU55
3900 | 63 | IDU56
3963 | 63 | IDU57
4026 | 63 | IDU58
4089 | 63 | IDU59
4152 | 63 | IDU60
4215 | 63 | IDU61
4278 | 63 | IDU62
4341 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
4343 | 1 | Data Type | For Engineering data 'E' = 0x45 For User data 'U' = 0x55
4344 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
4346 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
4350 | 1 | # | End of Data
4351 | Total No of Bytes

## DVRF ODU Parameters
Frame From PC Monitoring to ODU Masters for ODU Parameters
* ¦ P¦ B ¦ Frame Count ¦ Data ¦ Protocol Version ¦ CRC¦ #
NOTE: 1. for Slave1 & Slave2, 1) PERF, 2)CHKM , 3)SLTM , 4)SLTL , 5)DMDL parameters are not used. So, keep these parameter text boxes disabled in PC software. And send 0x30 for above parameters in protocol bytes which will be ignored while data processing at Slave ODU. 2. By default, mode selection for every parameter is Auto.
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | B | Broadcast Frame
3 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 88
6 | 1 | O | O=ODU
7 | 1 | P | P=Parameters
8 | 1 | System1 | If Bit=1 then ODU State=Active If Bit=0 then ODU State=Inactive Bit 0-> ODUm State Bit 1-> Slave1 State Bit 2-> Slave2 State Bit 3-> 0 e.g. if ODUm & Slave2 Active then D1=0x05 D1=0x35(ASCII)
9 | 1 | System2 | Bit 0-> ODUm State Bit 1-> Slave1 State Bit 2-> Slave2 State Bit 3-> 0
10 | 1 | System3
11 | 1 | System4
12 | 1 | System5
13 | 1 | System6
14 | 1 | System7
15 | 1 | System8
16 | 1 | System9
17 | 1 | System10
18 | 1 | System11
19 | 1 | System12
20 | 1 | System13
21 | 1 | System14
22 | 1 | System15
23 | 1 | System16
24 | 1 | System17
25 | 1 | System18
26 | 1 | System19
27 | 1 | System20
28 | 1 | System21
29 | 1 | System22
30 | 1 | System23
31 | 1 | System24
32 | 1 | System25
33 | 1 | System26
34 | 1 | System27
35 | 1 | System28
36 | 1 | System29
37 | 1 | System30
38 | 1 | System31
39 | 1 | System32
40 | 1 | System33
41 | 1 | System34
42 | 1 | System35
43 | 1 | System36
44 | 1 | System37
45 | 1 | System38
46 | 1 | System39
47 | 1 | System40
48 | 1 | System41
49 | 1 | System42
50 | 1 | System43
51 | 1 | System44
52 | 1 | System45
53 | 1 | System46
54 | 1 | System47
55 | 1 | System48
56 | 1 | System49
57 | 1 | System50
58 | 1 | System51
59 | 1 | System52
60 | 1 | System53
61 | 1 | System54
62 | 1 | System55
63 | 1 | System56
64 | 1 | System57
65 | 1 | System58
66 | 1 | System59
67 | 1 | System60
68 | 3 | PWM | Range:(0-1000)d=(0-3E8)h Remove one dec point frm pc i.e. /10 since range changed from 1000 to 100 (0x30,0x30,0x30 – 0x33,0x45,0x38)ASCII
71 | 1 | PWM Mode | 0x30 = Auto,0x31 = Manual
72 | 1 | Fix1Comp | 0x30 = OFF 0x31 = ON
73 | 1 | Fix1Comp Mode | 0x30 = Auto,0x31 = Manual
74 | 1 | Fix2Comp | 0x30 = OFF 0x31 = ON
75 | 1 | Fix2Comp Mode | 0x30 = Auto,0x31 = Manual
76 | 1 | 4W V | 0x30 = OFF 0x31 = ON
77 | 1 | 4W V Mode | 0x30 = Auto,0x31 = Manual
78 | 1 | SORV | 0x30 = OFF 0x31 = ON
79 | 1 | SORV Mode | 0x30 = Auto,0x31 = Manual
80 | 1 | OPOV | 0x30 = OFF 0x31 = ON
81 | 1 | OPOV Mode | 0x30 = Auto,0x31 = Manual
82 | 1 | ORCV | 0x30 = OFF 0x31 = ON
83 | 1 | ORCV Mode | 0x30 = Auto,0x31 = Manual
84 | 1 | LIBA | 0x30 = OFF 0x31 = ON
85 | 1 | LIBA Mode | 0x30 = Auto,0x31 = Manual
86 | 1 | LIA1 | 0x30 = OFF 0x31 = ON
87 | 1 | LIA1 Mode | 0x30 = Auto,0x31 = Manual
88 | 1 | LIA2 | 0x30 = OFF 0x31 = ON
89 | 1 | LIA2 Mode | 0x30 = Auto,0x31 = Manual
90 | 1 | EVIV | 0x30 = OFF 0x31 = ON display/disable this parameter on software screen
91 | 1 | EVIV Mode | 0x30 = Auto,0x31 = Manual display/disable this parameter on software screen
92 | 1 | MLQV | 0x30 = OFF 0x31 = ON
93 | 1 | MLQV Mode | 0x30 = Auto,0x31 = Manual
94 | 1 | HOTD | 0x30 = OFF 0x31 = ON
95 | 1 | HOTD Mode | 0x30 = Auto,0x31 = Manual
96 | 3 | EXV | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII
99 | 1 | EXV Mode
100 | 2 | IDUqty | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII
102 | 1 | IDUqty Mode | 0x30 = Auto,0x31 = Manual
103 | 1 | PERF | 0x30 = OFF 0x31 = ON
104 | 1 | PERF Mode | 0x30 = Auto,0x31 = Manual
105 | 1 | CHKM | 0x30 = OFF 0x31 = ON
106 | 1 | CHKM Mode | 0x30 = Auto,0x31 = Manual
107 | 1 | SLTM | 0x30 = OFF 0x31 = ON
108 | 1 | SLTM Mode | 0x30 = Auto,0x31 = Manual
109 | 1 | SLTL | 0x30 = OFF 0x31 = ON
110 | 1 | SLTL Mode | 0x30 = Auto,0x31 = Manual
111 | 1 | DMDL | 0x30 = OFF 0x31 = ON
112 | 1 | DMDL Mode | 0x30 = Auto,0x31 = Manual
113 | 1 | MODE | 0x30 = setFREE 0x31 = setHEAT 0x32 = setCOOL
114 | 1 | ODU MODE Mode | 0x30 = Auto,0x31 = Manual
115 | 2 | FanSp | Range: (0=11)d=(0-B)h=(0x30,0x42)ASCII
117 | 1 | FanSp Mode | 0x30 = Auto,0x31 = Manual
118 | 8 | Set Date | Byte1 = D Byte2 = D Byte3 = M Byte4 = M Byte5 = Y Byte6 = Y Byte7 = Y Byte8 = Y
126 | 1 | Set Date Mode | 0x30 = Auto,0x31 = Manual
127 | 6 | Set Time | Byte1 = H Byte2 = H Byte3 = M Byte4 = M Byte5 = S Byte6 = S
133 | 1 | Set Time Mode | 0x30 = Auto,0x31 = Manual
134 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
136 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
140 | 1 | # | End of Data
141 | Total No of Bytes

## MVRF Engineering Frame
Command Frame From PC Monitoring to ODU Master of System for Engineering Data
* ¦ P¦ C ¦ Frame Count ¦ Syatem ID ¦ Command¦ Data Type(E) ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | C | Command Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | C
5 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
7 | 2 | Command | For System Status Data 01d=(01)h=(0x30,0x31)ASCII
9 | 1 | Data Type | For Engineering data 'E' = 0x45
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17
Reply Send from ODU Master of System to PC Monitoring for User data
* ¦ M¦ D ¦ XXF ¦ System Data ¦ Syatem ID¦ Data Type(E) ¦ Protocol Version no ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame From Master to PC monitoring
2 | 1 | D | Data Frame
3 | 3 | XXF | Freematch
6 |  | System Info
6 | 1 | System 3min OFF | 0x30 = OFF 0x31 = ON Bool
7 | 2 | IDUqty | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned Char
9 | 3 | ΣODU | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII Unsigned int
12 | 4 | ΣIDU | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCIIt Unsigned int
16 | 3 | Diversity | Range:(0-150)d=(provision for 0-999)d= (0x30,0x30,0x30-0x33,0x45,0x37)ASCII Unsigned int
19 | 4 | ΣThermoON | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
23 | 4 | TMC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
27 | 4 | TSCnew | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
31 | 4 | TSCold | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
35 | 4 | BTCnew | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII Unsigned int
39 | 4 | BTCold | Range:(0-2112)d=(0x30,0x30,0x30 – 0x38,0x34,0x30)ASCII Unsigned int
43 | 1 | ODU Mode | 0x30 = Off 0x31 = Heat 0x32 = Cool 0x33 = Free Unsigned char
44 | 1 | ODU Mode Act | 0x30 = Off 0x31 = Heat 0x32 = Cool Unsigned char
45 | 10 | ODU RTC | DD:MM:YY, HH:MM
55 |  | Switch
55 | 1 | PERF | 0x30 = OFF 0x31 = ON Bool
56 | 1 | CHKM | (0-15)d = (0-F)h Unsigned Char
57 | 1 | SLTM
58 | 1 | SLTL
59 | 1 | DMDM
60 | 1 | DMDL
61 |  | General Info Master
61 | 1 | CAP | 0x30 = '0' = 0 HP 0x31 = '1' = 3 HP 0x32 = '2' = 4 HP 0x33 = '3' = 5 HP 0x34 = '4' = 6 HP 0x35 = '5' = 8 HP Unsigned Char
62 | 4 | TOC | Range:(0-21824)d=(0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30)ASCII Unsigned int
66 | 1 | Defrost | 0x30 = Normal 0x31 = Go defrost Unsigned Char
67 | 3 | DBG | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII Unsigned int
70 | 1 | ODU 3 min OFF | 0x30 = OFF 0x31 = ON Bool
71 | 1 | Inv 3 min off
72 | 4 | Nominal Capacity
76 | 4 | Max Capacity
80 | 3 | ECC | Range : (0-704)d=(0-2C0)h= (0x30,0x30,0x30-0x32,0x43,0x30)ASCII Unsigned int
83 | 2 | Master F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
85 | 2 | Drive F/w | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char
87 |  | Master Output
87 | 3 | Set RPS | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
90 | 3 | F/b RPS | Decimal Range :(0-1000)d=(0-3E8)h Unsigned int
93 | 1 | 4W V | 0x30 = OFF 0x31 = ON Bool
94 | 1 | SV1
95 | 1 | CCH
96 | 1 | PFC status
97 | 1 | Digital O/p
98 | 1 | Extra O/p
99 | 1 | Fan Speed | 0x30 = OFF 0x31 = Low 0x32 = High
100 | 3 | EXV Step | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII Unsigned int
103 |  | Master Inputs
103 | 3 | DLT | Range: (0 – 150)d=(0-096)h (0x30,0x30,0x30 – 0x30,0x39,0x36)ASCII Unsigned int
106 | 4 | Tgas | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int
110 | 4 | T mid
114 | 4 | Tliq
| 4 | Extra
118 | 4 | Tamb
122 | 2 | Err | For Example C4=0x43,0x34 E1=0x45,0x31 F2=0x46,0x32 U4=0x55,0x34 Unsigned Char
124 | 2 | Last err
126 | 4 | Warning | 0-65535 [0-ffff]
130 | 4 | Last Warning | 0-65535 [0-ffff]
134 | 4 | Inv Current | 0-65535 [0-ffff]
138 | 4 | AC Input current | 0-65535 [0-ffff]
134 | 4 | Input Current limit | 0-65535 [0-ffff]
138 | 4 | Shutdown error code 1 | 0-65535 [0-ffff]
142 | 4 | Shutdown error code 2 | 0-65535 [0-ffff]
146 | 4 | Warning error code | 0-65535 [0-ffff]
150 | 4 | Heat Sink Temperature | 0-65535 [0-ffff]
154 | 4 | Heat sink overheat warning value | 0-65535 [0-ffff]
158 | 4 | AC Input Voltage | 0-65535 [0-ffff]
162 | 4 | DC Bus Voltage | 0-65535 [0-ffff]
166 | 4 | Drive output voltage | 0-65535 [0-ffff]
170 | 4 | Maximum frequency | 0-65535 [0-ffff]
174 | 1 | Driver working status | 0-9[0-9]
175 |  | Protection Master
175 | 1 | HP SW | 0x30 = OFF 0x31 = ON Bool
176 | 1 | LP SW
177 | 1 | Tc
178 | 1 | Te
179 | 1 | DLT
180 | 1 | Inv_Phase_Lack_Protection
181 | 1 | Inv_DC_UV_OV_Protection
182 | 1 | Inv_AC_Vtg_Protection
183 | 1 | Inv Current Protection(CP)
184 | 1 | Freqn_Not_Raise_Or_Drop_Status
185 | 1 | Inv IPM Temp Protection(IT)
186 | 1 | IPM_Sensor_Failure_Protection
187 |  | Master Pretrip Counts
187 | 1 | Pretrip_Count_For_Current_Protection | (0-15)d = (0-F)h Unsigned Char
188 | 1 | Pretrip_Count_For_Phase_Lack_Protection
189 | 1 | Pretrip_Count_For_IPM_Protection
190 | 100 | Reserved Bytes | 'X'
290 |  | IDU1
290 | 1 | IDU mode | 0x30=Fan 0x31=Heat 0x32=Cool 0x33=Dry Unsigned Char | 0
291 | 1 | IDU status | 0x30 = OFF 0x31 = ON Bool | 1
292 | 2 | IDU error code | Range:(U0-UF)=(0x55,0x30-0x55,0x46)ASCII Unsigned Char | 2
294 | 2 | DCL | Range:(0-101)d=(0x30,0x30-0x36,0x35)ASCII Unsigned Char | 4
296 | 3 | DeltaT | 1 byte for polarity ‘+’ = Positive ‘-‘ = Negative 2 bytes for Value Decimal range 0.0 to 5.0 (give dec point frm pc by/10) For communication range is 0 to 50 (0x30,0x30-0x33,0x32)ASCII 1st Byte sign 3 Bytes Unsigned Int | 6
299 | 4 | Troom | Temperature Range:-15.0 to 60.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc by/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | 9
303 | 4 | Tliq | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | 13
307 | 1 | IDU capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw 0x4C = 'L' = 44.0Kw 0x4D = 'M' = 52.7Kw 0x4E = 'N' = 70.3Kw 0x4F = 'O' = 87.9Kw 0x50 = 'P' = 105.5Kw | 17
308 | 1 | Model name | 0x31 = HiWall 2TR 0x32 = Ducted 0x33 = 4Way 0x34 = Mini 4Way 0x35 = Ceiling Concealed 0x36 = Floor 0x37 = TFA 0x38 = Heat Recovery 0x39 = HiWall 1.5TR | 18
309 | 4 | Tsupply | Temperature Range: -45.0 to +140.0 1 byte for polarity ‘+’ = Positive = 0x2B ‘-‘ = Negative = 0x2D 3 bytes for value Decimal range : 0.0 to 140.0 Range: (0 to 1400)d=(0 to 0x578)h give dec point frm pc y/10 (0x30,0x30,0x30 – 0x35,0x37,0x38) 1st Byte sign 3 Bytes Unsigned Int | 19
313 | 4 | Tgas |  | 23
317 | 1 | Thermostat on/off | 0x30 = OFF 0x31 = ON Bool | 27
318 | 1 | Set Fan Speed by ODU | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 =M 0x34 = H 0x35 = Free Unsigned Char | 28
319 | 1 | Actual Fan Speed |  | 29
320 | 2 | user set | Range: (0-30)d=(0x30,0x30-0x31,0x45)ASCII Unsigned Char | 30
322 | 1 | pump on/off | 0x30 = OFF 0x31 = ON Bool | 32
323 | 1 | flap position | 0x30 = Swing 0x31 = F1 0x32 = F2 0x33 = F3 0x34 = F4 0x35 = F5 Unsigned Char | 33
324 | 1 | swing on/off | 0x30 = OFF 0x31 = ON Bool | 34
325 | 5 | EXV step of IDU | Decimal Range : -520 to 520 Total 5bytes1 for polarity +’ = Positive ‘-‘ = Negative 'a' = absolute And4 bytes for value Range:(0 to520)d=(0-208)h (0x30x30,0x30,0x30 – 0x32,0x30,0x38)ASCII 1st Byte sign 4 Bytes Unsigned Int | 35
330 | 4 | delta Tcoil | Decimal range: -20.0 to 30.0 °C with resolution of 0.5 Total 4 bytes1 byte for polarity‘ +’ = Positive ‘-‘ = Negative And3 bytes for value Range: 0.0 to 30.0 (0 to 300)d=(0-12C)h (0x30,0x30,0x30 to 0x31,0x32,0x43)ASCII 1st Byte sign 3 Bytes Unsigned Int | 40
334 | 1 | Set Fan Speed By IDU | 0x30 = Stop 0x31 = LL 0x32 = L 0x33 = M 0x34 = H 0x35 = Free Unsigned Char | 44
335 | 1 | IDU 1 min OFF | 0x30 = OFF 0x31 = ON Bool | 45
336 | 1 | Door Key Status |  | 46
337 | 2 | IDU Program Version | (01-256)d=(01-FF)h=(0x30,0x31-0x46,0x46)ASCII Unsigned Char | 47
339 | 1 | IDU on Lock | 0x30 = Unlocked 0x31 = Locked Bool | 49
340 | 1 | IDU off Lock | 0x30 = Unlocked 0x31 = Locked Bool | 50
341 | 1 | IDU Mode Lock | 0x30 = Unlocked 0x31 = Locked Bool | 51
342 | 1 | IDU Temp Lock | 0x30 = Unlocked 0x31 = Locked Bool | 52
343 | 4 | Start Time | 2Byte for Hour 2Byte for Minute Unsigned int | 53
347 | 4 | End Time | 2Byte for Hour 2Byte for Minute Unsigned int | 57
351 | 1 | Sleep Mode | 0x30 = OFF 0x31 = ON Bool | 61
352 | 1 | Drain Pump Lock | 0x30 = Unlocked 0x31 = Locked Bool | 62
353 | 1 | Door Key Lock | 0x30 = Unlocked 0x31 = Locked Bool | 63
354 | 1 | IDU Future bytes | 'X' | 64
355 |  |  |  | 65
355 | 65 | IDU2 | All 63 Bytes are same as IDU1
420 | 65 | IDU3
485 | 65 | IDU4
550 | 65 | IDU5
615 | 65 | IDU6
680 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII Unsigned Char
682 | 1 | Data Type | For Engineering data 'E' = 0x45 For User data 'U' = 0x55
683 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII Unsigned Char
685 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission Unsigned int
689 | 1 | # | End of Data
690 | Total No of Bytes

## MVRF ODU Parameters
Frame From PC Monitoring to ODU Masters for ODU Parameters
* ¦ P¦ B ¦ Frame Count ¦ Data ¦ Protocol Version ¦ CRC¦ #
NOTE: 1. By default, mode selection for every parameter is Auto. 2. For Reserved Bytes - respective Mode field will always be Auto 3. Slave 1, Slave 2, Slave 3 does not exist.
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | B | Broadcast Frame
3 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 88
6 | 1 | O | O=ODU
7 | 1 | P | P=Parameters
8 | 1 | System1 | If Bit=1 then ODU State=Active If Bit=0 then ODU State=Inactive Bit 0-> ODUm State Bit 1-> Slave1 State Bit 2-> Slave2 State Bit 3-> 0 e.g. if ODUm & Slave2 Active then D1=0x05 D1=0x35(ASCII)
9 | 1 | System2 | Bit 0-> ODUm State Bit 1-> Slave1 State Bit 2-> Slave2 State Bit 3-> 0
10 | 1 | System3
11 | 1 | System4
12 | 1 | System5
13 | 1 | System6
14 | 1 | System7
15 | 1 | System8
16 | 1 | System9
17 | 1 | System10
18 | 1 | System11
19 | 1 | System12
20 | 1 | System13
21 | 1 | System14
22 | 1 | System15
23 | 1 | System16
24 | 1 | System17
25 | 1 | System18
26 | 1 | System19
27 | 1 | System20
28 | 1 | System21
29 | 1 | System22
30 | 1 | System23
31 | 1 | System24
32 | 1 | System25
33 | 1 | System26
34 | 1 | System27
35 | 1 | System28
36 | 1 | System29
37 | 1 | System30
38 | 1 | System31
39 | 1 | System32
40 | 1 | System33
41 | 1 | System34
42 | 1 | System35
43 | 1 | System36
44 | 1 | System37
45 | 1 | System38
46 | 1 | System39
47 | 1 | System40
48 | 1 | System41
49 | 1 | System42
50 | 1 | System43
51 | 1 | System44
52 | 1 | System45
53 | 1 | System46
54 | 1 | System47
55 | 1 | System48
56 | 1 | System49
57 | 1 | System50
58 | 1 | System51
59 | 1 | System52
60 | 1 | System53
61 | 1 | System54
62 | 1 | System55
63 | 1 | System56
64 | 1 | System57
65 | 1 | System58
66 | 1 | System59
67 | 1 | System60
68 | 3 | RPS | Range:(0-1000)d=(0-3E8)h Remove one dec point frm pc i.e. /10 since range changed from 1000 to 100 (0x30,0x30,0x30 – 0x33,0x45,0x38)ASCII
71 | 1 | RPS Mode | 0x30 = Auto,0x31 = Manual
72 | 1 | SV1 | 0x30 = OFF 0x31 = ON
73 | 1 | SV1 Mode | 0x30 = Auto,0x31 = Manual
74 | 1 | PFC | 0x30 = OFF 0x31 = ON
75 | 1 | PFC Mode | 0x30 = Auto,0x31 = Manual
76 | 1 | 4W V | 0x30 = OFF 0x31 = ON
77 | 1 | 4W V Mode | 0x30 = Auto,0x31 = Manual
78 | 1 | Reserved 1 | 0x30 = OFF 0x31 = ON
79 | 1 | Reserved 1 Mode | 0x30 = Auto,0x31 = Manual
80 | 1 | Reserved 2 | 0x30 = OFF 0x31 = ON
81 | 1 | Reserved 2 Mode | 0x30 = Auto,0x31 = Manual
82 | 1 | Reserved 3 | 0x30 = OFF 0x31 = ON
83 | 1 | Reserved 3 Mode | 0x30 = Auto,0x31 = Manual
84 | 1 | Reserved 4 | 0x30 = OFF 0x31 = ON
85 | 1 | Reserved 4 Mode | 0x30 = Auto,0x31 = Manual
86 | 1 | Reserved 5 | 0x30 = OFF 0x31 = ON
87 | 1 | Reserved 5 Mode | 0x30 = Auto,0x31 = Manual
88 | 1 | Reserved 6 | 0x30 = OFF 0x31 = ON
89 | 1 | Reserved 6 Mode | 0x30 = Auto,0x31 = Manual
90 | 1 | Reserved 7 | 0x30 = OFF 0x31 = ON display/disable this parameter on software screen
91 | 1 | Reserved 7 Mode | 0x30 = Auto,0x31 = Manual display/disable this parameter on software screen
92 | 1 | Reserved 8 | 0x30 = OFF 0x31 = ON
93 | 1 | Reserved 8 Mode | 0x30 = Auto,0x31 = Manual
94 | 1 | Reserved 9 | 0x30 = OFF 0x31 = ON
95 | 1 | Reserved 9 Mode | 0x30 = Auto,0x31 = Manual
96 | 3 | EXV | Decimal Range : (0 – 520)d=(0-208)h (0x30,0x30,0x30 – 0x32,0x30,0x38)ASCII
99 | 1 | EXV Mode
100 | 2 | Reserved 10 | Range (0-64)d=(0-40)h=(0x30,0x30-0x34,0x30)ASCII
102 | 1 | Reserved 10 Mode | 0x30 = Auto,0x31 = Manual
103 | 1 | PERF | 0x30 = OFF 0x31 = ON
104 | 1 | PERF Mode | 0x30 = Auto,0x31 = Manual
105 | 1 | CHKM | 0x30 = OFF 0x31 = ON
106 | 1 | CHKM Mode | 0x30 = Auto,0x31 = Manual
107 | 1 | SLTM | 0x30 = OFF 0x31 = ON
108 | 1 | SLTM Mode | 0x30 = Auto,0x31 = Manual
109 | 1 | SLTL | 0x30 = OFF 0x31 = ON
110 | 1 | SLTL Mode | 0x30 = Auto,0x31 = Manual
111 | 1 | DMDL | 0x30 = OFF 0x31 = ON
112 | 1 | DMDL Mode | 0x30 = Auto,0x31 = Manual
113 | 1 | Set ODU MODE | 0x30 = setFREE 0x31 = setHEAT 0x32 = setCOOL
114 | 1 | ODU MODE Mode | 0x30 = Auto,0x31 = Manual
115 | 2 | FanSp | 0x30 = OFF 0x31 = Low 0x32 = High
117 | 1 | FanSp Mode | 0x30 = Auto,0x31 = Manual
118 | 8 | Set Date | Byte1 = D Byte2 = D Byte3 = M Byte4 = M Byte5 = Y Byte6 = Y Byte7 = Y Byte8 = Y
126 | 1 | Set Date Mode | 0x30 = Auto,0x31 = Manual
127 | 6 | Set Time | Byte1 = H Byte2 = H Byte3 = M Byte4 = M Byte5 = S Byte6 = S
133 | 1 | Set Time Mode | 0x30 = Auto,0x31 = Manual
134 | 2 | Reserved 11 | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
136 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
140 | 1 | # | End of Data
141 | Total No of Bytes

## MVRF Configuration Download
Frame From PC Monitoring to ODU Master for Configuration Download Request
* ¦ P¦ C ¦ Frame Count ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | C | Command Frame
3 | 2 | No. of characters in the Frame before CRC including '*' =in Hex= | B
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 2 | Command | For System Configuration Download 02d=(02)h=(0x30,0x32)ASCII
9 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
11 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
15 | 1 | # | End of Data
16 | Total No of Bytes
Reply From ODU Master to PC Monitoring for Configuration Download
* ¦ M¦ O ¦ XXI¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Frame From ODU Master to PC Monitoring
2 | 1 | O | Configuration Data
3 | 3 | XXF | Freematch
6 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
8 |  | ODU Master Configuration
8 | 1 | Master | 0x30
9 | 2 | IDU Quantity | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
11 | 1 | ODU Quantity | 0x30
12 | 1 | ODU Address | 0x31
13 | 1 | ODU Capacity | 0x30 = '0' = 0 HP 0x31 = '1' = 3 HP 0x32 = '2' = 4 HP 0x33 = '3' = 5 HP 0x34 = '4' = 6 HP 0x35 = '5' = 8 HP Unsigned Char
14 | 1 | Silent Mode | 0x30= Not Effect 0x31= Always ON 0x32= Select Timer
15 | 1 | Silent Level | 0x30=High 0x31=Low
16 | 1 | Heat/Cool/Free | 0x30=FREE 0x31=HEAT 0x32=COOL
17 | 1 | Comp. Backup | 0x30=Digital 0x31=Fix1 0x32=Fix2 0x33=ODU
18 | 1 | Demand Mode | 0x30= No control 0x31=Always as per level 0x32=As per timer
19 | 1 | Demand Level | 0x30=0 0x31=1 0x32=2 0x33=3
20 | 1 | Test (Performance) | 0x30=0 0x31=1 0x32=2 0x33=3 0x34=4
21 | 2 | Group No. | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
23 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
39 |  | ODU Slave1 Configuration
39 | 1 | Slave1 | 0x30
40 | 2 | IDU Quantity | 0x30
42 | 1 | ODU Quantity | 0x30
43 | 1 | ODU Address | 0x30
44 | 1 | ODU Capacity | 0x30
45 | 1 | Silent Mode | 0x30
46 | 1 | Silent Level | 0x30
47 | 1 | Heat/Cool/Free | 0x30
48 | 1 | Comp. Backup | 0x30
49 | 1 | Demand Mode | 0x30
50 | 1 | Demand Level | 0x30
51 | 1 | Test (Performance) | 0x30
52 | 2 | Group No. | 0x30
54 | 16 | Label | 0x30
70 |  | ODU Slave2 Configuration
70 | 1 | Slave2 | 0x30
71 | 2 | IDU Quantity | 0x30
73 | 1 | ODU Quantity | 0x30
74 | 1 | ODU Address | 0x30
75 | 1 | ODU Capacity | 0x30
76 | 1 | Silent Mode | 0x30
77 | 1 | Silent Level | 0x30
78 | 1 | Heat/Cool/Free | 0x30
79 | 1 | Comp. Backup | 0x30
80 | 1 | Demand Mode | 0x30
81 | 1 | Demand Level | 0x30
82 | 1 | Test (Performance) | 0x30
83 | 2 | Group No. | 0x30
85 | 16 | Label | 0x30
101 |  | IDU Configuration
101 | 2 | IDU1 ID | (01)d=(01)h=(0x30,0x31)ASCII
103 | 1 | IDU Type | 0x31 = HiWall 2TR 0x32 = Ducted 0x33 = 4Way 0x34 = Mini 4Way 0x35 = Ceiling Concealed 0x36 = Floor 0x37 = TFA 0x38 = Heat Recovery 0x39 = HiWall 1.5TR
104 | 1 | IDU Capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw
105 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
121 | 20 | IDU2 | IDU ID = 02
141 | 20 | IDU3 | IDU ID = 03
161 | 20 | IDU4 | IDU ID = 04
181 | 20 | IDU5 | IDU ID = 05
201 | 20 | IDU6 | IDU ID = 06
221 | 20 | IDU7 | 0x30
241 | 20 | IDU8 | 0x30
261 | 20 | IDU9 | 0x30
281 | 20 | IDU10 | 0x30
301 | 20 | IDU11 | 0x30
321 | 20 | IDU12 | 0x30
341 | 20 | IDU13 | 0x30
361 | 20 | IDU14 | 0x30
381 | 20 | IDU15 | 0x30
401 | 20 | IDU16 | 0x30
421 | 20 | IDU17 | 0x30
441 | 20 | IDU18 | 0x30
461 | 20 | IDU19 | 0x30
481 | 20 | IDU20 | 0x30
501 | 20 | IDU21 | 0x30
521 | 20 | IDU22 | 0x30
541 | 20 | IDU23 | 0x30
561 | 20 | IDU24 | 0x30
581 | 20 | IDU25 | 0x30
601 | 20 | IDU26 | 0x30
621 | 20 | IDU27 | 0x30
641 | 20 | IDU28 | 0x30
661 | 20 | IDU29 | 0x30
681 | 20 | IDU30 | 0x30
701 | 20 | IDU31 | 0x30
721 | 20 | IDU32 | 0x30
741 | 20 | IDU33 | 0x30
761 | 20 | IDU34 | 0x30
781 | 20 | IDU35 | 0x30
801 | 20 | IDU36 | 0x30
821 | 20 | IDU37 | 0x30
841 | 20 | IDU38 | 0x30
861 | 20 | IDU39 | 0x30
881 | 20 | IDU40 | 0x30
901 | 20 | IDU41 | 0x30
921 | 20 | IDU42 | 0x30
941 | 20 | IDU43 | 0x30
961 | 20 | IDU44 | 0x30
981 | 20 | IDU45 | 0x30
1001 | 20 | IDU46 | 0x30
1021 | 20 | IDU47 | 0x30
1041 | 20 | IDU48 | 0x30
1061 | 20 | IDU49 | 0x30
1081 | 20 | IDU50 | 0x30
1101 | 20 | IDU51 | 0x30
1121 | 20 | IDU52 | 0x30
1141 | 20 | IDU53 | 0x30
1161 | 20 | IDU54 | 0x30
1181 | 20 | IDU55 | 0x30
1201 | 20 | IDU56 | 0x30
1221 | 20 | IDU57 | 0x30
1241 | 20 | IDU58 | 0x30
1261 | 20 | IDU59 | 0x30
1281 | 20 | IDU60 | 0x30
1301 | 20 | IDU61 | 0x30
1321 | 20 | IDU62 | 0x30
1341 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
1343 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
1347 | 1 | # | End of Data
1348 | Total No of Bytes

## MVRF Configuration Upload
From PC Monitoring to ODU Master for Configuration Upload
* ¦ P ¦ D ¦ Frame Count ¦ Data ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | From PC Monitoring to ODU Master
2 | 1 | O | Congiguration Data
3 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | 53F
6 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
8 |  | ODU Master Configuration
8 | 1 | Master | 0x30
9 | 2 | IDU Quantity | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
11 | 1 | ODU Quantity | 0x30
12 | 1 | ODU Address | 0x31
13 | 1 | ODU Capacity | 0x30 = '0' = 0 HP 0x31 = '1' = 3 HP 0x32 = '2' = 4 HP 0x33 = '3' = 5 HP 0x34 = '4' = 6 HP 0x35 = '5' = 8 HP Unsigned Char
14 | 1 | Silent Mode | 0x30= Not Effect 0x31= Always ON 0x32= Select Timer
15 | 1 | Silent Level | 0x30=High 0x31=Low
16 | 1 | Heat/Cool/Free | 0x30=FREE 0x31=HEAT 0x32=COOL
17 | 1 | Comp. Backup | 0x30=Digital 0x31=Fix1 0x32=Fix2 0x33=ODU
18 | 1 | Demand Mode | 0x30= No control 0x31=Always as per level 0x32=As per timer
19 | 1 | Demand Level | 0x30=0 0x31=1 0x32=2 0x33=3
20 | 1 | Test (Performance) | 0x30=0 0x31=1 0x32=2 0x33=3 0x34=4
21 | 2 | Group No. | (01-64)d=(01-40)h=(0x30,0x31-0x34,0x30)
23 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
39 |  | ODU Slave1 Configuration
39 | 1 | Slave1 | 0x30
40 | 2 | IDU Quantity | 0x30
42 | 1 | ODU Quantity | 0x30
43 | 1 | ODU Address | 0x30
44 | 1 | ODU Capacity | 0x30
45 | 1 | Silent Mode | 0x30
46 | 1 | Silent Level | 0x30
47 | 1 | Heat/Cool/Free | 0x30
48 | 1 | Comp. Backup | 0x30
49 | 1 | Demand Mode | 0x30
50 | 1 | Demand Level | 0x30
51 | 1 | Test (Performance) | 0x30
52 | 2 | Group No. | 0x30
54 | 16 | Label | 0x30
70 |  | ODU Slave2 Configuration
70 | 1 | Slave2 | 0x30
71 | 2 | IDU Quantity | 0x30
73 | 1 | ODU Quantity | 0x30
74 | 1 | ODU Address | 0x30
75 | 1 | ODU Capacity | 0x30
76 | 1 | Silent Mode | 0x30
77 | 1 | Silent Level | 0x30
78 | 1 | Heat/Cool/Free | 0x30
79 | 1 | Comp. Backup | 0x30
80 | 1 | Demand Mode | 0x30
81 | 1 | Demand Level | 0x30
82 | 1 | Test (Performance) | 0x30
83 | 2 | Group No. | 0x30
85 | 16 | Label | 0x30
101 |  | IDU Configuration
101 | 2 | IDU1 ID | (01)d=(01)h=(0x30,0x31)ASCII
103 | 1 | IDU Type | 0x31 = HiWall 2TR 0x32 = Ducted 0x33 = 4Way 0x34 = Mini 4Way 0x35 = Ceiling Concealed 0x36 = Floor 0x37 = TFA 0x38 = Heat Recovery 0x39 = HiWall 1.5TR
104 | 1 | IDU Capacity | 0x31 = '1' = 2.8Kw 0x32 = '2' = 3.5Kw 0x33 = '3' = 4.6Kw 0x34 = '4' = 5.3Kw 0x35 = '5' = 7.0Kw 0x36 = '6' = 7.7Kw 0x37 = '7' = 8.8Kw 0x38 = '8' = 10.5Kw 0x39 = '9' = 12.3Kw 0x40 = '@' = 14.1Kw 0x41 = 'A' = 17.6Kw 0x42 = 'B' = 19.3Kw 0x43 = 'C' = 21.1Kw 0x44 = 'D' = 23.9Kw 0x45 = 'E' = 28.1Kw 0x46 = 'F' = 35.2Kw 0x47 = 'G' = 2.3Kw 0x48 = 'H' = 6.0Kw 0x49 = 'I' = 8.1Kw 0x4A = 'J' = 10.0Kw 0x4B = 'K' = 11.3Kw
105 | 16 | Label | Alphanumeric Label of 16 characters (A-Z)=0x41-0x5A (a-z)=0x61-0x7A (0-9)=0x30-0x39
121 | 20 | IDU2 | IDU ID = 02
141 | 20 | IDU3 | IDU ID = 03
161 | 20 | IDU4 | IDU ID = 04
181 | 20 | IDU5 | IDU ID = 05
201 | 20 | IDU6 | IDU ID = 06
221 | 20 | IDU7 | 0x30
241 | 20 | IDU8 | 0x30
261 | 20 | IDU9 | 0x30
281 | 20 | IDU10 | 0x30
301 | 20 | IDU11 | 0x30
321 | 20 | IDU12 | 0x30
341 | 20 | IDU13 | 0x30
361 | 20 | IDU14 | 0x30
381 | 20 | IDU15 | 0x30
401 | 20 | IDU16 | 0x30
421 | 20 | IDU17 | 0x30
441 | 20 | IDU18 | 0x30
461 | 20 | IDU19 | 0x30
481 | 20 | IDU20 | 0x30
501 | 20 | IDU21 | 0x30
521 | 20 | IDU22 | 0x30
541 | 20 | IDU23 | 0x30
561 | 20 | IDU24 | 0x30
581 | 20 | IDU25 | 0x30
601 | 20 | IDU26 | 0x30
621 | 20 | IDU27 | 0x30
641 | 20 | IDU28 | 0x30
661 | 20 | IDU29 | 0x30
681 | 20 | IDU30 | 0x30
701 | 20 | IDU31 | 0x30
721 | 20 | IDU32 | 0x30
741 | 20 | IDU33 | 0x30
761 | 20 | IDU34 | 0x30
781 | 20 | IDU35 | 0x30
801 | 20 | IDU36 | 0x30
821 | 20 | IDU37 | 0x30
841 | 20 | IDU38 | 0x30
861 | 20 | IDU39 | 0x30
881 | 20 | IDU40 | 0x30
901 | 20 | IDU41 | 0x30
921 | 20 | IDU42 | 0x30
941 | 20 | IDU43 | 0x30
961 | 20 | IDU44 | 0x30
981 | 20 | IDU45 | 0x30
1001 | 20 | IDU46 | 0x30
1021 | 20 | IDU47 | 0x30
1041 | 20 | IDU48 | 0x30
1061 | 20 | IDU49 | 0x30
1081 | 20 | IDU50 | 0x30
1101 | 20 | IDU51 | 0x30
1121 | 20 | IDU52 | 0x30
1141 | 20 | IDU53 | 0x30
1161 | 20 | IDU54 | 0x30
1181 | 20 | IDU55 | 0x30
1201 | 20 | IDU56 | 0x30
1221 | 20 | IDU57 | 0x30
1241 | 20 | IDU58 | 0x30
1261 | 20 | IDU59 | 0x30
1281 | 20 | IDU60 | 0x30
1301 | 20 | IDU61 | 0x30
1321 | 20 | IDU62 | 0x30
1341 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
1343 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
1347 | 1 | # | End of Data
1348 | Total No of Bytes
ACK or NACK Frame From ODU Master to PC Monitoring
* ¦ M ¦ A ¦ XI ¦ System ID ¦ Frame Count ¦ Protocol Version ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | M | Bootloader Frame
2 | 1 | A / N | 'A' = Ack frame 'N' = Nack frame
3 | 2 | XI | IVRF
5 | 2 | System ID | (01 - 60)d=(01- 3C)h=(0x30,0x31 - 0x33,0x43)ASCII
7 | 3 | No. of characters in the Frame before CRC including '*' =in Hex= | C
10 | 2 | Protocol Revision | Range:(0-256)d=(0-FF)h=(0x30,0x30-0x46,0x46)ASCII
12 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
16 | 1 | # | End of Data
17 | Total No of Bytes

## PC-ODU Interaction Algorithm
INTERACTION ALGORITHM 1.1 INITIATION OF COMMUNICATION All communication will be initiated by PC Monitoring software as Master. 1.2 RULES OF COMMUNICATION 1. All communication will happen using the serial interface (RS485) at 57600-8-N-1. 2. All communication will be initiated by PC Monitoring. The ODU Master of requested system will send data frame if CRC matched else send the NACK frame as reply. Once data frame is received by PC, PC will update data if CRC is matched. 3. 16 bit CRC calculated including 'Start of frame'. It will be in ASCII hex format so 4 bytes will be required for it. All bytes in a frame will be in ASCII hex format.
PC Comm frame | System ID1 | System ID2
User Frame | *PC0C0101U0145A1# | *PC0C0201U0176A1#
Eng Frame | *PC0C0101E0180A0# | *PC0C0201E01B3A0#
Config frame | *PC0B010201B1C8# | *PC0B020201B18C#
Start of bl | *B1000100FC0101D8FE#
BL progr | *B10001215C02222222FFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFFF010E0E#
bl polling | *B1000100FC0301185F# | *BA000100ER1012C80# | *BA000100ER001ECD1#
end of bl | *B1000100FC0401D9EE# | Successful Reply | Failed Reply
User frame | *MD7064+0F00+0000+0000000000321003220900000000000000XXXXX2100+0EBD221100010000000000X2100+0EBC421120000000000000X2100+0F0F221100000000000000X0000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000001U034AAE#
Engg Frame | *MD0FA41C2047+33-090000000F01180F0+127+05A+118+163+0F00000000000+00+00000000000000000+000+000+000+000+0000000000000+00+00000000000000000+000+000+000+000+00000001B1000000006101E01E00000000000000000000001E01E00000000000000000000001E01E000000003210032209700000000000000000000000000202400D30000007000000000000000006D0000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000000010100200300000180000XXXXX210064+46+0F0+0F0D2+000+0F015211101a0000+000201020010000000000X210064+73+0EB+0EBC4+000+0F015211120a0000+004201020000000000000X210064+46+0F0+0F0F2+000+0F015211101a0000+000201020000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X000000+00+000+00011+000+00005000001a0000+000000000000000000000X01E03BAC5#
74 |  |  | 178-180 | 3 | PWMC | Decimal Range :0-1000 | give dec point form pc by/10
0x33,0x45,0x38
| b) | SLAVE1
75 |  |  | 181-183 | 3 | PWM | Decimal Range :0-1000 | give dec point form pc by/10
0x33,0x45,0x38
76 |  |  | 184 | 1 | Fix1 | 0x30 = OFF
0x31 = ON
77 |  |  | 185 | 1 | Fix2 | 0x30 = OFF
0x31 = ON
78 |  |  | 186 | 1 | 4W V | 0x30 = OFF
0x31 = ON
79 |  |  | 187 | 1 | SORV | 0x30 = OFF
0x31 = ON
80 |  |  | 188 | 1 | OPOV | 0x30 = OFF
0x31 = ON
81 |  |  | 189 | 1 | ORCV | 0x30 = OFF
0x31 = ON
82 |  |  | 190 | 1 | LIBA | 0x30 = OFF
0x31 = ON
83 |  |  | 191 | 1 | LIA1 | 0x30 = OFF
0x31 = ON
84 |  |  | 192 | 1 | LIA2 | 0x30 = OFF
0x31 = ON
85 |  |  | 193 | 1 | EVIV | 0x30 = OFF
0x31 = ON
86 |  |  | 194 | 1 | MLQV | 0x30 = OFF
0x31 = ON
87 |  |  | 195 | 1 | HOTD | 0x30 = OFF
0x31 = ON
88 |  |  | 196-198 | 3 | EXV Step | Decimal Range : 0 – 520
ASCII hex range : 0x30,0x30,0x30 – 0x32,0x30,0x38
89 |  |  | 199-201 | 3 | EXV Step | Decimal Range : 0 – 520
ASCII hex range : 0x30,0x30,0x30 – 0x32,0x30,0x38
90 |  |  | 202-204 | 3 | Fan speed rpm | 0-1000rpm
0x30,0x30,0x30-0x33,0x45,0x38
91 |  |  | 205-207 | 3 | PWMC | Decimal Range :0-1000 | give dec point from pc by/10
0x33,0x45,0x38
| c) | SLAVE2
92 |  |  | 208-210 | 3 | PWM | Decimal Range :0-1000 | give dec point from pc by/10
0x33,0x45,0x38
93 |  |  | 211 | 1 | Fix1 | 0x30 = OFF
0x31 = ON
94 |  |  | 212 | 1 | Fix2 | 0x30 = OFF
0x31 = ON
95 |  |  | 213 | 1 | 4W V | 0x30 = OFF
0x31 = ON
96 |  |  | 214 | 1 | SORV | 0x30 = OFF
0x31 = ON
97 |  |  | 215 | 1 | OPOV | 0x30 = OFF
0x31 = ON
98 |  |  | 216 | 1 | ORCV | 0x30 = OFF
0x31 = ON
99 |  |  | 217 | 1 | LIBA | 0x30 = OFF
0x31 = ON
100 |  |  | 218 | 1 | LIA1 | 0x30 = OFF
0x31 = ON
101 |  |  | 219 | 1 | LIA2 | 0x30 = OFF
0x31 = ON
102 |  |  | 220 | 1 | EVIV | 0x30 = OFF
0x31 = ON
103 |  |  | 221 | 1 | MLQV | 0x30 = OFF
0x31 = ON
104 |  |  | 222 | 1 | HOTD | 0x30 = OFF
0x31 = ON
105 |  |  | 223-225 | 3 | EXV Step | Decimal Range : 0 – 520
ASCII hex range : 0x30,0x30,0x30 – 0x32,0x30,0x38
106 |  |  | 226-228 | 3 | EXV Step | Decimal Range : 0 – 520
ASCII hex range : 0x30,0x30,0x30 – 0x32,0x30,0x38
107 |  |  | 229-231 | 3 | Fan speed rpm | 0-1000rpm
0x30,0x30,0x30-0x33,0x45,0x38
108 |  |  | 232-234 | 3 | PWMC | Decimal Range :0-1000 | give dec point from pc by/10
0x33,0x45,0x38
C) | SYSTEM
| a) | SYSTEM
109 |  |  | 235-236 | 2 | IDUqty | Decimal Range : 1-64
ASCII hex range : 0x30,0x31 – 0x33,0x45
110 |  |  | 237-239 | 3 | SUMkw ODU | 0-2112 | give dec point from pc by/10
ASCII hex range : 0x30,0x30,0x30 – 0x38,0x34,0x30
111 |  |  | 240-243 | 4 | SUMkw IDU | 0-21824 | give dec point from pc by/10
ASCII hex range : 0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30
112 |  |  | 244-246 | 3 | Diversity | 0-150(provision for 0-999) 0x30,0x39,0x36
113 |  |  | 247-250 | 4 | SUMkw IDU Thermo ON | 0-21824 | give dec point from pc by/10
ASCII hex range : 0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30
114 |  |  | 251-252 | 2 | DCLmax | 0-101
ASCII hex range:0x30,0x30 – 0x36,0x35
115 |  |  | 253-256 | 4 | TMC | 0-21824
[6 empty] | ASCII hex range : 0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30 | give dec point from pc by/10
116 |  |  | 257-260 | 4 | TSCnew | 0-21824
[6 empty] | ASCII hex range : 0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30 | give dec point from pc by/10
117 |  |  | 261-264 | 4 | TSCold | 0-21824
[6 empty] | ASCII hex range : 0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30 | give dec point from pc by/10
118 |  |  | 265-268 | 4 | BTCnew | 0-2112
[6 empty] | ASCII hex range : 0x30,0x30,0x30 – 0x38,0x34,0x30 | give dec point from pc by/10
119 |  |  | 269-272 | 4 | BTCold | 0-2112
[6 empty] | ASCII hex range : 0x30,0x30,0x30 – 0x38,0x34,0x30 | give dec point from pc by/10
120 |  |  | 273 | 1 | ODU Mode | 0x30 = Off
0x31 = Heat
0x32 = Cool
0x33 = Free
121 |  |  | 274 | 1 | Defrost | 0x30 = Normal operation
0x31 = Go defrost
122 |  |  | 275 | 1 | ODU Mode Act | 0x30 = Off
0x31 = Heat
0x32 = Cool
D) | GENERAL
| a) | MASTER
123 |  | Delete | 274 | 1 | CAP | 0x30 = 0,0x31 = 12 HP,0x32 = 14 HP,0x33 = 16 HP,0x34 = 18 HP,0x35 = 21 HP,0x36 = 24 HP
124 |  |  | 275-278 | 4 | TOC | Decimal Range :0-21824 | give dec point from pc by/10
ASCII hex range : 0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30
125 |  | Delete | 279 | 1 | Defrost | 0x30 = Normal operation
0x31 = Go defrost
126 |  |  | 280 | 1 | Self oil recovery | 0x30 = Normal
0x31 = Do self oil recovery
127 |  |  | 281 | 1 | Oil Swap | 0x30 = Normal operation
0x31 = Supplier
0x32 = receiver
128 |  |  | 282 | 1 | Liquid inject | 0x30 = OFF
0x31 = ON
129 |  |  | 283 | 1 | vaccum injection valve | 0x30 = OFF,0x31 = ON
130 |  | Delete | 284-286 | 3 | EXV Step | Decimal Range : 0 – 520
ASCII hex range : 0x30,0x30,0x30 – 0x32,0x30,0x38
131 |  |  | 287 | 1 | ODU 3 min OFF | 0x30 = OFF
0x31 = ON
132 |  |  | 288 | 1 | Fix1 3 min off | 0x30 = OFF
0x31 = ON
133 |  |  | 289 | 1 | Fix2 3 min off | 0x30 = OFF
0x31 = ON
134 |  |  | 290-291 | 2 | Err | e.g-0xE6
135 |  |  | 292-293 | 2 | Last err | e.g-0xE6
136 |  |  | 294 | 4 | CAPnew | 0x30 = 0,0x31 = 12 HP,0x32 = 14 HP,0x33 = 16 HP,0x34 = 18 HP,0x35 = 21 HP,0x36 = 24 HP
137 |  |  | 295 | 4 | CAPold | 0x30 = 0,0x31 = 12 HP,0x32 = 14 HP,0x33 = 16 HP,0x34 = 18 HP,0x35 = 21 HP,0x36 = 24 HP
138 |  |  | 296-298 | 3 | ECC | Decimal Range : 0-704
ASCII hex range : 0x30,0x30,0x30 – 0x32,0x43,0x30
| b) | SLAVE1
139 |  |  | 299 | 1 | CAP | 0x30 = 0,0x31 = 12 HP,0x32 = 14 HP,0x33 = 16 HP,0x34 = 18 HP,0x35 = 21 HP,0x36 = 24 HP
140 |  |  | 300-303 | 4 | TOC | Decimal Range :0-21824 | give dec point from pc by/10
ASCII hex range : 0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30
141 |  |  | 304 | 1 | Defrost | 0x30 = Normal operation
0x31 = Go defrost
142 |  |  | 305 | 1 | Self oil recovery | 0x30 = Normal
0x31 = Do self oil recovery
143 |  |  | 306 | 1 | Oil Swap | 0x30 = Normal operation
0x31 = Supplier
0x32 = receiver
144 |  |  | 307 | 1 | Liquid inject | 0x30 = OFF
0x31 = ON
145 |  |  | 308 | 1 | vaccum injection valve | 0x30 = OFF,0x31 = ON
146 |  |  | 309-311 | 3 | EXV Step | Decimal Range : 0 – 520
ASCII hex range : 0x30,0x30,0x30 – 0x32,0x30,0x38
147 |  |  | 312 | 1 | ODU 3 min OFF | 0x30 = OFF
0x31 = ON
148 |  |  | 313 | 1 | Fix1 3 min off | 0x30 = OFF
0x31 = ON
149 |  |  | 314 | 1 | Fix2 3 min off | 0x30 = OFF
0x31 = ON
150 |  |  | 315-316 | 2 | Err | e.g-0xE6
151 |  |  | 317-318 | 2 | Last err | e.g-0xE6
152 |  |  | 319 | 1 | CAPnew | 0x30 = 0,0x31 = 12 HP,0x32 = 14 HP,0x33 = 16 HP,0x34 = 18 HP,0x35 = 21 HP,0x36 = 24 HP
153 |  |  | 320 | 1 | CAPold | 0x30 = 0,0x31 = 12 HP,0x32 = 14 HP,0x33 = 16 HP,0x34 = 18 HP,0x35 = 21 HP,0x36 = 24 HP
154 |  |  | 321-323 | 3 | ECC | Decimal Range : 0-704
ASCII hex range : 0x30,0x30,0x30 – 0x32,0x43,0x30
| c) | SLAVE2
|  |  | 324 | 1 | CAP | 0x30 = 0,0x31 = 12 HP,0x32 = 14 HP,0x33 = 16 HP,0x34 = 18 HP,0x35 = 21 HP,0x36 = 24 HP
|  |  | 325-328 | 4 | TOC | Decimal Range :0-21824 | give dec point from pc by/10
ASCII hex range : 0x30,0x30,0x30,0x30 – 0x35,0x35,0x34,0x30
|  |  | 329 | 1 | Defrost | 0x30 = Normal operation
0x31 = Go defrost
|  |  | 330 | 1 | Self oil recovery | 0x30 = Normal
0x31 = Do self oil recovery
|  |  | 331 | 1 | Oil Swap | 0x30 = Normal operation
0x31 = Supplier
0x32 = receiver
|  |  | 332 | 1 | Liquid inject | 0x30 = OFF
0x31 = ON
|  |  | 333 | 1 | vaccum injection valve | 0x30 = OFF,0x31 = ON
|  |  | 334-336 | 3 | EXV Step | Decimal Range : 0 – 520
ASCII hex range : 0x30,0x30,0x30 – 0x32,0x30,0x38
|  |  | 337 | 1 | ODU 3 min OFF | 0x30 = OFF
0x31 = ON
|  |  | 338 | 1 | Fix1 3 min off | 0x30 = OFF
0x31 = ON
|  |  | 339 | 1 | Fix2 3 min off | 0x30 = OFF
0x31 = ON
|  |  | 340-341 | 2 | Err | e.g-0xE6
|  |  | 342-343 | 2 | Last err | e.g-0xE6
|  |  | 344 | 1 |  | 0x30 = 0,0x31 = 12 HP,0x32 = 14 HP,0x33 = 16 HP,0x34 = 18 HP,0x35 = 21 HP,0x36 = 24 HP
|  |  | 345 | 1 |  | 0x30 = 0,0x31 = 12 HP,0x32 = 14 HP,0x33 = 16 HP,0x34 = 18 HP,0x35 = 21 HP,0x36 = 24 HP
|  |  | 346-348 | 3 |  | Decimal Range : 0-704
ASCII hex range : 0x30,0x30,0x30 – 0x32,0x43,0x30
E) | PROTECTION
| a) | MASTER
|  |  | 349 | 1 | Error Absent/Present | 0x30 = OFF,0x31 = ON
|  |  | 350 | 1 | Error Absent/Present | 0x30 = OFF,0x31 = ON
|  |  | 351 | 1 | Error Absent/Present | 0x30 = OFF,0x31 = ON
|  |  | 352 | 1 | Error Absent/Present | 0x30 = OFF,0x31 = ON
|  |  | 353 | 1 | Error Absent/Present | 0x30 = OFF
0x31 = ON
|  |  | 354 | 1 | over current | 0x30 = OFF,0x31 = ON
|  |  | 355 | 1 | phase reversal | 0x30 = OFF,0x31 = ON
|  |  | 356 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 357 | 1 | single phasing | 0x30 = OFF,0x31 = ON
|  |  | 358 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 359 | 1 | under voltage | 0x30 = OFF,0x31 = ON
|  |  | 360 | 1 | over voltage | 0x30 = OFF,0x31 = ON
| b) | SLAVE1
|  |  | 361 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 362 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 363 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 364 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 365 | 1 |  | 0x30 = OFF
0x31 = ON
|  |  | 366 | 1 | over current | 0x30 = OFF,0x31 = ON
|  |  | 367 | 1 | phase reversal | 0x30 = OFF,0x31 = ON
|  |  | 368 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 369 | 1 | single phasing | 0x30 = OFF,0x31 = ON
|  |  | 370 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 371 | 1 | under voltage | 0x30 = OFF,0x31 = ON
|  |  | 372 | 1 | over voltage | 0x30 = OFF,0x31 = ON
| c) | SLAVE2
|  |  | 373 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 374 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 375 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 376 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 377 | 1 |  | 0x30 = OFF
0x31 = ON
|  |  | 378 | 1 | over current | 0x30 = OFF,0x31 = ON
|  |  | 379 | 1 | phase reversal | 0x30 = OFF,0x31 = ON
|  |  | 380 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 381 | 1 | single phasing | 0x30 = OFF,0x31 = ON
|  |  | 382 | 1 |  | 0x30 = OFF,0x31 = ON
|  |  | 383 | 1 | under voltage | 0x30 = OFF,0x31 = ON
|  |  | 384 | 1 | over voltage | 0x30 = OFF,0x31 = ON
F) | PRIORITIES
| a) | MASTER
|  |  | 385 | 1 | priority disable/enable | 0x30 = DISABLE
0x31 = ENABLE
|  |  | 386 | 1 | priority disable/enable | 0x30 = DISABLE
0x31 = ENABLE
|  |  | 387 | 1 | compressor start | 0x30 = DISABLE
0x31 = ENABLE
| b) | SLAVE1
|  |  | 388 | 1 | priority disable/enable | 0x30 = DISABLE
0x31 = ENABLE
|  |  | 389 | 1 | priority disable/enable | 0x30 = DISABLE
0x31 = ENABLE
|  |  | 390 | 1 | compressor start | 0x30 = DISABLE
0x31 = ENABLE
| c) | SLAVE2
|  |  | 391 | 1 | priority disable/enable | 0x30 = DISABLE
0x31 = ENABLE
|  |  | 392 | 1 | priority disable/enable | 0x30 = DISABLE
0x31 = ENABLE
|  |  | 393 | 1 | compressor start | 0x30 = DISABLE
0x31 = ENABLE
G) | SWITCH
| a) | MASTER
|  |  | 394 | 1 | performance mode on/off | 0x30 = OFF
0x31 = ON
|  |  | 395 | 1 | check mode | 0x30 = OFF
0x31 = ON
|  |  | 396 | 1 | silent mode | 0x30 = 0
0x31 = 1, 0x32 = 2
|  |  | 397 | 1 | Silent Level | 0x30 = OFF
0x31 = ON
|  |  | 398 | 1 | Demand Level | 0x30 = 0
0x31 = 1, 0x32 = 2, 0x33 = 3
| b) | SLAVE1
|  |  |  | NA | NA
|  |  |  | NA | NA
|  |  |  | NA | NA
|  |  |  | NA | NA
|  |  |  | NA | NA
| c) | SLAVE2
|  |  |  | NA | NA
|  |  |  | NA | NA
|  |  |  | NA | NA
|  |  |  | NA | NA
|  |  |  | NA | NA
IDU1
|  |  | 399 | 1 | IDU mode | 0x30 = Fan
0x31 = Heat
0x32 = Cool
0x33 = Dry
|  |  | 400 | 1 | IDU status | 0x30 = Off
0x31 = On
|  |  | 401-402 | 2 | IDU error code | not defined E6
|  |  | 403-404 | 2 | DCL | Decimal range: 0 – 101
ASCII hex range:0x30,0x30 – 0x36,0x35
|  |  | 405-407 | 3 | DeltaT | 1 byte for polarity | give dec point from pc by/10
‘+’ = Positive
‘-‘ = Negative
And
2 bytes for Value
Decimal range 0.0 to 5.0
For communication range is 0 to 50
Hex range 0x00 to 0x32
ASCII range 0x30,0x30 to
0x33,0x32
|  |  | 408-411 | 4 | Troom | Range: -15.0 to 60.0 °C with resolution of 0.5 | give dec point from pc by/10
Total 4 bytes
1 byte for polarity
‘+’ = Positive
‘-‘ = Negative
And
3 bytes for value
Decimal range : 0.0 to 60.0
For communication range is 0 to 600
ASCII hex range: 0 to 0x258
0x30,0x30,0x30 – 0x32,0x35,0
|  |  | 412-415 | 4 | Tliq | Range: -45.0 to 140.0 °C with resolution of 0.5 | -ve temperature sign,give dec point from pc by/10
Total 4 bytes
1 byte for polarity
‘+’ = Positive
‘-‘ = Negative
And
3 bytes for value
Decimal range : 0.0 to 140.0
For communication range is 0 to 1400
ASCII hex range: 0 to 0x578
0x30,0x30,0x30 – 0x35,0x3
|  |  | 416 | 1 | IDU capacity | 0x31 = 2.8
0x32 = 3.5
0x33 = 4.6
0x34 = 5.3
0x35 = 7.0
0x36 = 7.7
0x37 = 8.8
0x38 = 10.6
0x39 = 12.3
0x40 = 14.1
0x41 = 17.6
0x42 = 19.3
0x43 = 21.1
0x44 = 23.9
0x45 = 28.1
0x46 = 35.2
|  |  | 417 | 1 | Model name | 0x31 = Hi wall
0x32 = Ducted
0x33 = 4 way
0x34 = Mini 4 way
0x35 = Ceiling concealed
0x36 = Floor
0x37 = TFA
0x38 = Heat recovery
|  |  | 418-421 | 4 | Tsupply | Range: -45.0 to 140.0 °C with resolution of 0.5 | give dec point from pc by/10
Total 4 bytes
1 byte for polarity
‘+’ = Positive
‘-‘ = Negative
And
3 bytes for value
Decimal range : 0.0 to 140.0
For communication range is 0 to 1400
ASCII hex range: 0 to 0x578
0x30,0x30,0x30 – 0x35,0x3
|  |  | 422-425 | 4 | Tgas | Range: -45.0 to 140.0 °C with resolution of 0.5 | -ve temperature sign,give dec point from pc by/10
Total 4 bytes
1 byte for polarity
‘+’ = Positive
‘-‘ = Negative
And
3 bytes for value
Decimal range : 0.0 to 140.0
For communication range is 0 to 1400
ASCII hex range: 0 to 0x578
0x30,0x30,0x30 – 0x35,0x3
|  |  | 426 | 1 | Thermostat on/off | 0x30 = OFF
0x31 = ON
|  |  | 427 | 1 | Fan control | 0x30 = Stop
0x31 = LL
0x32 = L
0x33 =M
0x34 = H
0x35 = Free
|  |  | 428 | 1 | Fan control | 0x30 = Stop
0x31 = LL
0x32 = L
0x33 =M
0x34 = H
0x35 = Free
|  |  | 429-430 | 2 | user set | Decimal range: 0-30
0x30,0x30-0x31,0x45
|  |  | 431 | 1 | pump on/off | 0x30 = OFF
0x31 = ON
|  |  | 432 | 1 | flap position | Decimal range: 1-5
0x31-0x35
|  |  | 433 | 1 | swing on/off | 0x30 = OFF
0x31 = ON
|  |  | 434-438 | 5 | EXV step of IDU | Decimal Range : -520 to 520
Total 5bytes
1 for polarity
+’ = Positive
‘-‘ = Negative
'a' = absolute And
4 bytes for value
ASCII hex range: 0 to 0x208
0x00,0x00,0x00 – 0x32,0x30,0x38
|  |  | 439-442 | 4 | delta coil | Decimal range: -20.0 to 30.0 °C with resolution of 0.5
Total 4 bytes
1 byte for polarity
‘+’ = Positive
‘-‘ = Negative
And
3 bytes for value
Decimal range: 0.0 to 30.0
For communication range is 0 to 300
ASCII hex range 0 to 0x12C
0x30,0x30,0x30 – 0x31,0
IDU2
443
IDU3
487
IDU4
531
IDU5
575
IDU6
619
IDU7
663
IDU8
707
IDU9
751
IDU10
795
IDU11
839
IDU12
883
IDU13
927
IDU14
971
IDU15
1015
IDU16
1059
IDU17
1103
IDU18
1147
IDU19
1191
IDU20
1235
| Total Bytes |  | 1278

## Miscellaneous Info
Command Frame From ATE / PCM / Debugger to ODU Master for Miscellaneous Information
* ¦ P ¦ M ¦ I ¦ System ID ¦ CRC ¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P | Frame from PC Monitoring to ODU Master
2 | 1 | M | Miscellaneous
3 | 1 | I | Information
4 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
6 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission
10 | 1 | # | End of Data
11
Reply Send from ODU Master
* ¦ P ¦ M ¦ I ¦ System ID ¦ System Type ¦ Data ¦ CRC¦ #
Protocol_Data Byte No. | Length (Bytes) | Parameter | Description
0 | 1 | * | Start of frame
1 | 1 | P
2 | 1 | M
3 | 3 | I
6 | 2 | System ID | (1-60)d=(1-3C)h=(0x30,0x30 to 0x33,0x43)ASCII
8 | 1 | System Type | D' - DVRF 'I' - IVRF 'F' - Freematch
9 |  | Master Data
9 | 2 | SPPR F/w | 0 to FF. Convert Ascii to Hex
11 | 2 | ODU Fan F/w | 0 to FF. Convert Ascii to Hex
13 | 2 | ODU Control F/w | 0 to FF. Convert Ascii to Hex
15 | 2 | Inverter Drive 1 F/w | 0 to FF. Convert Ascii to Hex
17 | 2 | Inverter Drive 2 F/w | 0 to FF. Convert Ascii to Hex
19 | 10 | Reserved Bytes | X'
29 |  | Slave 1 Data
29 | 2 | SPPR F/w | 0 to FF. Convert Ascii to Hex
31 | 2 | ODU Fan F/w | 0 to FF. Convert Ascii to Hex
33 | 2 | ODU Control F/w | 0 to FF. Convert Ascii to Hex
35 | 2 | Inverter Drive 1 F/w | 0 to FF. Convert Ascii to Hex
37 | 2 | Inverter Drive 2 F/w | 0 to FF. Convert Ascii to Hex
39 | 10 | Reserved Bytes | X'
49 |  | Slave 2 Data
49 | 2 | SPPR F/w | 0 to FF. Convert Ascii to Hex
51 | 2 | ODU Fan F/w | 0 to FF. Convert Ascii to Hex
53 | 2 | ODU Control F/w | 0 to FF. Convert Ascii to Hex
55 | 2 | Inverter Drive 1 F/w | 0 to FF. Convert Ascii to Hex
57 | 2 | Inverter Drive 2 F/w | 0 to FF. Convert Ascii to Hex
59 | 10 | Reserved Bytes | X'
69 |  | Slave 3 Data
69 | 2 | SPPR F/w | 0 to FF. Convert Ascii to Hex
71 | 2 | ODU Fan F/w | 0 to FF. Convert Ascii to Hex
73 | 2 | ODU Control F/w | 0 to FF. Convert Ascii to Hex
75 | 2 | Inverter Drive 1 F/w | 0 to FF. Convert Ascii to Hex
77 | 2 | Inverter Drive 2 F/w | 0 to FF. Convert Ascii to Hex
79 | 10 | Reserved Bytes | X'
89 | 200 | Reserved Bytes | X'
289 | 4 | CRC | 16 bit CRC calculated from including * and converted to 4 byte ASCII hex for transmission Unsigned int
293 | 1 | # | End of Data
294 | Total No of Bytes